## Sheet1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | B2425
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | B2425 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Post anaesthetic recovery of patients. 2) Medical and nursing procedures. 3) Observation is undertaken by medical and nursing staff. 4) Clinical wash-hand basin may be used. 5) Mobile equipment and services may be used. 6) Moving/ Manoeuvring beds. 7) Monitoring/diagnostic or therapeutic equipment may be used. 8) Piped medical gases, vacuum and associated equipment may be used.
| Personnel: | [6 empty] | 1 x patient. 1 x staff. 1 x other.
| Planning Relationships: | [5 empty] | Part of multi-bay area. Overall area to include staff communication base and utilities. Close to operating theatre.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 14 |  |  |  |  | Height (mm): |  |  |  | 2700
2700 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | The call repeat lamp is situated outside of the bay. A staff emergency call linked to an emergency call repeat lamp in the staff communications base and each operating theatre required. Note the engineering services included in this data sheet comply with the requirements of HTM 08-03 and superseded the text in para 4.154 of HBN 26-1 and 3.175 of HBN 10-02. For dedicated maternity recovery may only include 1 no. of each s outlet. The following items are shown on the room layout but are optional: - cleaning socket outlet may be shared between multiple bays (9m max cable); - light switch for multiple bay space. The following items may be provided: - when used for maternity provision of a cot(s) may be required; - ceiling-mounted hoist, subject to local policy; - lead protection for mobile imaging, subject to RPA advice. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
B2425
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | B2425 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 500 |  | WP
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
| Standby Lighting Grade - Local Lighting: | [13 empty] | A
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45 |  | The LAmax,f dB noise limit applies only at night 23:00 to 07:00 hours.
| Noise Intrusion (dB) 1hr night: | [13 empty] | 35
| Noise Intrusion (dB) f night: | [13 empty] | 45
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | B2425
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | B2425 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England. All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | B2425
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | B2425 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL035 |  | LAMP repeat call (patient/staff or staff emergency or Cardiac call), ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | IMG002 |  | MONITOR medical display 18"; digital image viewer, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG058 |  | LUMINAIRE, examination, wall, adjustable, 1000 lux | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | RAI130 |  | RAIL, clinical equipment, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRA106 |  | TRACK, curtain, one sided, 4000mm length | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BRA015 |  | BRACKET, flat panel monitor, height adjustable, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL020 |  | HOLDER, sharps box, up to 7 litre capacity, rail/trolley hang or wall mounted, 170H 125W 100D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT002 |  | TROLLEY, modular storage, single open frame, including handle and worktop, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | B2425
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | B2425 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | STO006 |  | STOOL, surgeon/anaesthetist, height adjustable, includes anti-static seat pads | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | B2425-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | B2425-01 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Post anaesthetic recovery of patients. 2) Medical and nursing procedures. 3) Observation is undertaken by medical and nursing staff. 4) Clinical wash-hand basin may be used. 5) Mobile equipment and services may be used. 6) Moving/ Manoeuvring beds. 7) Monitoring/diagnostic or therapeutic equipment may be used. 8) Piped medical gases, vacuum and associated equipment may be used.
| Personnel: | [6 empty] | 1 x patient. 1 x staff. 1 x other.
| Planning Relationships: | [5 empty] | Part of multi-bay area. Overall area to include staff communication base and utilities. Close to operating theatre.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 14 |  |  |  |  | Height (mm): |  |  |  | 2700
2700 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | The call repeat lamp is situated outside of the bay. A staff emergency call linked to an emergency call repeat lamp in the staff communications base and each operating theatre required. Note the engineering services included in this data sheet comply with the requirements of HTM 08-03 and superseded the text in para 4.154 of HBN 26-1 and 3.175 of HBN 10-02. For dedicated maternity recovery may only include 1 no. of each s outlet. The following items are shown on the room layout but are optional: - cleaning socket outlet may be shared between multiple bays (9m max cable); The following items may be provided: - when used for maternity provision of a cot(s) may be required; - ceiling-mounted hoist, subject to local policy; - lead protection for mobile imaging, subject to RPA advice. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
B2425-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | B2425-01 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 500 |  | WP
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
| Standby Lighting Grade - Local Lighting: | [13 empty] | A
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45 |  | The LAmax,f dB noise limit applies only at night 23:00 to 07:00 hours.
| Noise Intrusion (dB) 1hr night: | [13 empty] | 35
| Noise Intrusion (dB) f night: | [13 empty] | 45
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | B2425-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | B2425-01 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England. All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | B2425-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | B2425-01 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL035 |  | LAMP repeat call (patient/staff or staff emergency or Cardiac call), ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | IMG002 |  | MONITOR medical display 18"; digital image viewer, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG058 |  | LUMINAIRE, examination, wall, adjustable, 1000 lux | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | RAI130 |  | RAIL, clinical equipment, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRA180 |  | TRACK, curtain, two sided, L-shape, 3700L 3100W | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BRA015 |  | BRACKET, flat panel monitor, height adjustable, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL020 |  | HOLDER, sharps box, up to 7 litre capacity, rail/trolley hang or wall mounted, 170H 125W 100D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT002 |  | TROLLEY, modular storage, single open frame, including handle and worktop, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STO006 |  | STOOL, surgeon/anaesthetist, height adjustable, includes anti-static seat pads | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | B2522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | B2522 |  |  |  |  | Recovery/induction room: Paediatric, 2 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may be ambulant, in a wheelchair or on a trolley or bed 2) Patients to rest and recover after treatment. 3) Small items of equipment and sundries are stored. 4) Emergency resuscitation may take place. 5) Clinical hand washing may be undertaken.
| Personnel: | [6 empty] | 2x Patients 2x Staff 1x Other (escort or relative)
| Planning Relationships: | [5 empty] | Easy access to dirty utility. Easy access to consulting/treatment rooms.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 20 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Space for parking & manoeuvring trolley is required.
| ADB | [7 empty] | Room Environmental Data
B2522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | B2522 |  |  |  |  | Recovery/induction room: Paediatric, 2 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 500 |  | WP
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 500 |  | WP
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
| Standby Lighting Grade - Local Lighting: | [13 empty] | A
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45 |  | The LAmax,f dB noise limit applies only at night 23:00 to 07:00 hours.
| Noise Intrusion (dB) 1hr night: | [13 empty] | 35
| Noise Intrusion (dB) f night: | [13 empty] | 45
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | B2522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | B2522 |  |  |  |  | Recovery/induction room: Paediatric, 2 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley, wheelchair & equipment access (1500mm); Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Desirable - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England. All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | B2522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | B2522 |  |  |  |  | Recovery/induction room: Paediatric, 2 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CAL003 |  | PUSH BUTTON, patient/staff call (help) with socket for patient hand-held unit | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CAL029 |  | LAMP patient reassurance, wall mounted | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC182 |  | CABINET base, 600mm facing, with 2 shelves, 1 door hinged right, on plinth, o/a height 900 | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SNS757 |  | SINKTOP, single bowl, no tap holes, no overflow, right hand integral ribbed drainer, stainless steel, 1200W 650D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP359 |  | TAP, pillar, high neck, long lever, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS007 |  | DISPENSER, paper towel roll, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 3 |  |  | 3 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA318 |  | CHAIR, upright, with arms, upholstered, stacking, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COU007 |  | COUCH, examination/treatment, (2 section), with paper roll holder, variable height, retractable wheels | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LIG015 |  | LUMINAIRE observation/examination, mobile, 1000 lux | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STA142 |  | STAND, infusion, twin hook, breaks, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SUC004 |  | SUCTION UNIT, electric, portable, 350H 320W 340D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO133 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 750W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO310 |  | TROLLEY, emergency/resuscitation, complete with defibrillator, 955H 825W 575D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | C0728
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | C0728 |  |  |  |  | Investigation room: stress electrocardiography (ECG)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may undergo electrocardiogram (ECG) exercise stress test. 2) Test results are recorded 3) Clinical hand washing. 4) Patient may be ambulant with/without walking aids, in a wheelchair or requiring assistance. 5) Patient may undress/dress in privacy. 6) Hanging clothing. 7) Call systems may be used. 8) Monitoring/diagnostic or therapeutic equipment may be used. 9) Medical hand sanitizer may be used. 10) Telephone(s) may be used.
| Personnel: | [6 empty] | 1 x Patient 2 x Staff, occasionally 3 x staff 1 x Other (relative or chaperone)
| Planning Relationships: | [5 empty] | Close to consultation room(s).
| Space Data: | [6 empty] | Area (m²): |  |  |  | 16 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Lamp indicator call situated over door outside room Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
C0728
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | C0728 |  |  |  |  | Investigation room: stress electrocardiography (ECG)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | At equipment
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | C0728
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | C0728 |  |  |  |  | Investigation room: stress electrocardiography (ECG)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | C0728
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | C0728 |  |  |  |  | Investigation room: stress electrocardiography (ECG)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL003 |  | PUSH BUTTON, patient/staff call (help) with socket for patient hand-held unit | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL008 |  | PUSH BUTTON staff crash call, reset and integral/adjacent indicator lamp, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG073 |  | ILLUMINATED SIGN, 'Room in use' | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 7 |  |  | 7 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW072 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 1200W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC076 |  | SWITCH, 'Room in use' illuminated sign. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA302 |  | CHAIR, swivel, height adjustable, medium back, wipeable, 5 star base, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA391 |  | CHAIR, easy, reclining, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CRD016 |  | ECHOCARDIOGRAPHY MACHINE | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | EXE016 |  | EXERCISE TREADMILL | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STO004 |  | STOOL, height adjustable, swivel, mobile | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | D0205
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0205 |  |  |  |  | Rest room with beverage, snack preparation bay: 5 staff
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Rest and relaxation or sleeping. 2) Patient, relative or staff may be reading. 3) Preparing beverages and snacks. 4) Consuming beverages, meals and snacks. 5) Holding/ storing food in refrigerator. 6) Holding crockery and cutlery. 7) Washing up of crockery and cutlery. 8) Staff notices, information and/or messages may be displayed. 9) Informal staff discussions. 10) Hand washing.
| Personnel: | [6 empty] | 5 x Staff
| Planning Relationships: | [5 empty] | Part of staff accommodation.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 11 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
D0205
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0205 |  |  |  |  | Rest room with beverage, snack preparation bay: 5 staff
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 – 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V/EM
| Daytime General Service Illuminance (Lux): | [13 empty] | 50 |  | Floor
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 200 |  | On tables
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 300 |  | At servery counter
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | D0205
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0205 |  |  |  |  | Rest room with beverage, snack preparation bay: 5 staff
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | D0205
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0205 |  |  |  |  | Rest room with beverage, snack preparation bay: 5 staff
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAT002 |  | MINI KITCHEN (combined unit) with refrigerator and microwave, sink top, wall cabinet, cupboard and drawers, laminate backboard, 1970H 1200W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC073 |  | CABINET, upper, modular storage, for 600 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAT003 |  | WATER BOILER, 2.5 litre, electric, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | RAC091 |  | RACK, magazine, 3 shelves, floor standing, fixed to the wall, 1400H 900W 300D | [16 empty] | 2
| 3 |  |  | 3 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA318 |  | CHAIR, upright, with arms, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB056 |  | TABLE, occasional, round, 415H 610mm dia. | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | D0434-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0434-01 |  |  |  |  | Rest room with beverages & snack preparation bay: 10 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Rest and relaxation or sleeping. 2) Small amounts of dry goods are stored in cupboard(s). 3) Holding/ storing food in refrigerator. 4) Crockery and cutlery are washed mechanically. 5) Hand-rinse basin may be used. 6) Consuming beverages, meals and snacks. 7) People preparing beverages, meals and snacks. 8) Telephone may be used and messages taken. 9) Laptop computer(s) may be used.
| Personnel: | [6 empty] | 10 x persons..
| Planning Relationships: | [5 empty] | Staff use - located away from public areas.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 20.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The following items are shown on the room layout but are optional: - telephone outlet; - mini kitchen water boiler; - mini kitchen microwave. The following items may be provided: - cube lockers for personal belongings; - television, radio - generally not in staff rest areas; - water cooler, or access. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
D0434-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0434-01 |  |  |  |  | Rest room with beverages & snack preparation bay: 10 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 – 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V/EM
| Daytime General Service Illuminance (Lux): | [13 empty] | 50 |  | Floor
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 200 |  | On tables
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 300 |  | At servery counter
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | D0434-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0434-01 |  |  |  |  | Rest room with beverages & snack preparation bay: 10 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | D0434-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0434-01 |  |  |  |  | Rest room with beverages & snack preparation bay: 10 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP715 |  | CUPBOARD, base, including sink panel, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP731 |  | CUPBOARD/DRAWER UNIT, base, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT301 |  | OUTLET, cold water for equipment | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP359 |  | TAP, pillar, high neck, long lever, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAT003 |  | WATER BOILER, 2.5 litre, electric, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WRT221 |  | WORKTOP, dished, stainless steel, with integral centre sink bowl and 2 tap holes, 2100W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP252 |  | CUPBOARD, 2 adjustable shelves, wall mounted, 750H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP259 |  | CUPBOARD, space for built in microwave, wall mounted, 750H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | OVE016 |  | OVEN, microwave, capacity 18 litre, build in, (suitable for CUP259) | [16 empty] | 2
| 8 |  |  | 8 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF058 |  | REFRIGERATOR, capacity 160 litre, automatic defrost, stainless steel, underbench, external temperature gauge, lockable, on castors, 850H 610W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB007 |  | TABLE, 710H 900W 900D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | D0434-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0434-02 |  |  |  |  | Rest room with beverages & snack preparation bay: 15 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Rest and relaxation or sleeping. 2) Small amounts of dry goods are stored in cupboard(s). 3) Holding/ storing food in refrigerator. 4) Crockery and cutlery are washed mechanically. 5) Hand-rinse basin may be used. 6) People preparing beverages, meals and snacks. 7) Consuming beverages, meals and snacks. 8) Telephone may be used and messages taken. 9) Laptop computer(s) may be used.
| Personnel: | [6 empty] | 15 x persons..
| Planning Relationships: | [5 empty] | Staff use - located away from public areas.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 28 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The following items are shown on the room layout but are optional: - telephone outlet; - mini kitchen water boiler; - mini kitchen microwave. The following items may be provided: - cube lockers for personal belongings; - television, radio - generally not in staff rest areas; - water cooler, or access. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
D0434-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0434-02 |  |  |  |  | Rest room with beverages & snack preparation bay: 15 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 – 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V/EM
| Daytime General Service Illuminance (Lux): | [13 empty] | 50 |  | Floor
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 200 |  | On tables
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 300 |  | At servery counter
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | D0434-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0434-02 |  |  |  |  | Rest room with beverages & snack preparation bay: 15 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | D0434-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0434-02 |  |  |  |  | Rest room with beverages & snack preparation bay: 15 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP715 |  | CUPBOARD, base, including sink panel, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP731 |  | CUPBOARD/DRAWER UNIT, base, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT301 |  | OUTLET, cold water for equipment | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP359 |  | TAP, pillar, high neck, long lever, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAT003 |  | WATER BOILER, 2.5 litre, electric, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WRT221 |  | WORKTOP, dished, stainless steel, with integral centre sink bowl and 2 tap holes, 2100W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP252 |  | CUPBOARD, 2 adjustable shelves, wall mounted, 750H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP259 |  | CUPBOARD, space for built in microwave, wall mounted, 750H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | OVE016 |  | OVEN, microwave, capacity 18 litre, build in, (suitable for CUP259) | [16 empty] | 2
| 11 |  |  | 11 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF058 |  | REFRIGERATOR, capacity 160 litre, automatic defrost, stainless steel, underbench, external temperature gauge, lockable, on castors, 850H 610W 600D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB135 |  | TABLE, 710H 1500W 900D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | D0434-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0434-03 |  |  |  |  | Rest room with beverages & snack preparation bay: 20 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Rest and relaxation or sleeping. 2) Small amounts of dry goods are stored in cupboard(s). 3) Holding/ storing food in refrigerator. 4) Crockery and cutlery are washed mechanically. 5) Hand-rinse basin may be used. 6) Consuming beverages, meals and snacks. 7) People preparing beverages, meals and snacks. 8) Telephone may be used and messages taken. 9) Laptop computer(s) may be used.
| Personnel: | [6 empty] | 20 x persons..
| Planning Relationships: | [5 empty] | Staff use - located away from public areas.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 35.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The following items are shown on the room layout but are optional: - telephone outlet; - mini kitchen water boiler; - mini kitchen microwave. The following items may be provided: - cube lockers for personal belongings; - television, radio - generally not in staff rest areas; - water cooler, or access. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
D0434-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0434-03 |  |  |  |  | Rest room with beverages & snack preparation bay: 20 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 – 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V/EM
| Daytime General Service Illuminance (Lux): | [13 empty] | 50 |  | Floor
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 200 |  | On tables
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 300 |  | At servery counter
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | D0434-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0434-03 |  |  |  |  | Rest room with beverages & snack preparation bay: 20 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | D0434-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0434-03 |  |  |  |  | Rest room with beverages & snack preparation bay: 20 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP715 |  | CUPBOARD, base, including sink panel, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP731 |  | CUPBOARD/DRAWER UNIT, base, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT301 |  | OUTLET, cold water for equipment | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP359 |  | TAP, pillar, high neck, long lever, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAT003 |  | WATER BOILER, 2.5 litre, electric, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WRT221 |  | WORKTOP, dished, stainless steel, with integral centre sink bowl and 2 tap holes, 2100W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP252 |  | CUPBOARD, 2 adjustable shelves, wall mounted, 750H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP259 |  | CUPBOARD, space for built in microwave, wall mounted, 750H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | OVE016 |  | OVEN, microwave, capacity 18 litre, build in, (suitable for CUP259) | [16 empty] | 2
| 16 |  |  | 16 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF058 |  | REFRIGERATOR, capacity 160 litre, automatic defrost, stainless steel, underbench, external temperature gauge, lockable, on castors, 850H 610W 600D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB135 |  | TABLE, 710H 1500W 900D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | D0434-04
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0434-04 |  |  |  |  | Rest room: 30 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Rest and relaxation or sleeping. 2) Laptop computer(s) may be used. 3) Telephone may be used and messages taken.
| Personnel: | [6 empty] | 30 x persons..
| Planning Relationships: | [5 empty] | Staff use - located away from public areas. Easy access to pantry
| Space Data: | [6 empty] | Area (m²): |  |  |  | 45.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The following items may be provided: - cube lockers for personal belongings; - television, radio - generally not in staff rest areas; - water cooler, or access. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
D0434-04
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0434-04 |  |  |  |  | Rest room: 30 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 – 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V/EM
| Daytime General Service Illuminance (Lux): | [13 empty] | 50 |  | Floor
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 200 |  | On tables
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | D0434-04
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0434-04 |  |  |  |  | Rest room: 30 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | D0434-04
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D0434-04 |  |  |  |  | Rest room: 30 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 26 |  |  | 26 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 7 |  |  | 7 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB135 |  | TABLE, 710H 1500W 900D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | D1311
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D1311 |  |  |  |  | Overnight stay room (single)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Rest and relaxation or sleeping. 2) Laptop computer(s) may be used. 3) Visitor may choose to read, write, listen to radio, view TV or use telephone.
| Personnel: | [6 empty] | 1-2 x persons. Intermittent use.
| Planning Relationships: | [5 empty] | En-suite sanitary facilities. Close to beverage making facilities. Subject to local policy/compliance with Approved document M, the room may be associated with an ambulant or semi-ambulant en-suite.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 13 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following items are shown on the room layout but are optional: - medical oxygen, vacuum and call outlets but would only be expected when the room is used for "Rooming-in" in neonatal care; - wall mounted television may be omitted and/or replaced by bedhead entertainment system subject to policy. The following items may be provided: - the bed may include an additional pull out mattress underneath the bed, however, it should be noted that the room is not sized as a twin bed space and this should be the exception. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
D1311
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D1311 |  |  |  |  | Overnight stay room (single)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 150 |  | On working plane
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40 |  | The LAmax,f dB noise limit applies only at night 23:00 to 07:00 hours.
| Noise Intrusion (dB) 1hr night: | [13 empty] | 35
| Noise Intrusion (dB) f night: | [13 empty] | 45
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 30 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | D1311
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D1311 |  |  |  |  | Overnight stay room (single)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Essential Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | D1311
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | D1311 |  |  |  |  | Overnight stay room (single)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | LIG003 |  | LUMINAIRE, reading, adjustable arm, 100 watt | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT206 |  | SOCKET outlet television aerial, single. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BRA015 |  | BRACKET, flat panel monitor, height adjustable, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | TVM001 |  | TELEVISION monitor, colour, flat panel, small, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BED004 |  | BED, divan style, fixed height, with legs, 1950L 900W | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | BED030 |  | BED headboard single | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA306 |  | CHAIR, easy, low back, with open arms, upholstered, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA318 |  | CHAIR, upright, with arms, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MAT010 |  | MATTRESS, single divan, 1950L 900W | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB005 |  | TABLE, 710H 900W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB035 |  | TABLE, bedside,540H 450W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | WAR007 |  | WARDROBE, 1800H 400W 400D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0117
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0117 |  |  |  |  | Imaging room: Ultrasound, general, obstetric and gynaecological
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may arrive on foot in a wheelchair or on a trolley 2) Patient may arrive on a trolley or in a bed. 3) Patient is positioned or repositioned for examination. 4) Ultrasound examination. 5) Oxygen and vacuum services may be used for resuscitation. 6) Daily holding/sorting of documents, records, radiology films in clinical or diagnostic areas. 7) Holding linen supply. 8) Clinical hand washing. 9) Immediate reporting of ultrasound scanning. 10) Recording patient data/notes. 11) Visual display terminal(s) may be used. 12) Communicating by a ward or department (Two-way communication system) within and outside hospital (telephone). 13) Using gel warmer.
| Personnel: | [6 empty] | 3 x Staff Woman & accompanying person
| Planning Relationships: | [5 empty] | En-suite WC. Adjacent to changing area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 16 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Link to departmental computer management system. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0117
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0117 |  |  |  |  | Imaging room: Ultrasound, general, obstetric and gynaecological
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6 |  | No intrusive procedures
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | on bed - dimmable
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0117
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0117 |  |  |  |  | Imaging room: Ultrasound, general, obstetric and gynaecological
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 1 x personnel, wheelchair & equipment access (1000mm); 1 x personnel, bed, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Non-essential - Project Option Solar control. Blackout/dimout Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0117
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0117 |  |  |  |  | Imaging room: Ultrasound, general, obstetric and gynaecological
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO022 |  | HOOK, double, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG053 |  | LUMINAIRE, examination, ceiling, adjustable, 1000 lux | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT004 |  | OUTLET cable, fused, 13 amp, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC073 |  | CABINET, upper, modular storage, for 600 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW053 |  | WORKTOP, clinical, for 3 x 400 facing modular storage cabinets, 1365W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC001 |  | SWITCH 5amp ac single pole, 1 way, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC031 |  | SWITCH dimmer, fixed position, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WRT068 |  | WORKTOP, non-clinical, 1800W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA303 |  | CHAIR, swivel, height adjustable 540-790, tilting back, adjustable footrest, wipeable, 5 star base, on castors/glides | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA363 |  | CHAIR, height adjustable, with arms, high back, swivel, 5 star base, wipeable, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0117
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0117 |  |  |  |  | Imaging room: Ultrasound, general, obstetric and gynaecological
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COU010 |  | COUCH, examination/treatment, (3 section), variable height, retractable wheels, with paper roll holder | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CUP418 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 483W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL008 |  | HOLDER, sack with lid foot operated, large, freestanding, 960H 500W 415D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO135 |  | TROLLEY, dressing/equipment, 6 clear trays, buffered, 890H 510W 480D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | ULT017 |  | ULTRASOUND computed sonography, 128 channels, multi purpose, mobile, 1295H 635W 920D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | WAR051 |  | WARMER, ultrasound couplant gel, 200H 100W 150D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0119
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0119 |  |  |  |  | Imaging room: Ultrasound, general and minor interventional
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may arrive on foot in a wheelchair or on a trolley 2) Patient may arrive on a trolley or in a bed. 3) Patient is positioned or repositioned for examination. 4) Administration of sedation. 5) Interventional work or imaging procedure examination. 6) Invasive surgical procedures under ultrasound control, e.g. biopsy. 7) Holding working supplies of sterile items. 8) Preparing and use of sterile trays and packs. 9) Oxygen and vacuum services may be used for resuscitation. 10) Daily holding/sorting of documents, records, radiology films in clinical or diagnostic areas. 11) Holding linen supply. 12) Clinical hand washing. 13) Immediate reporting of ultrasound scanning. 14) Recording patient data/notes. 15) Visual display terminal(s) may be used. 16) Communicating by a ward or department (Two-way communication system) within and outside hospital (telephone). 17) Using gel warmer.
| Personnel: | [6 empty] | 1 x Patient 4 x Staff 1 - 2 trainee staff
| Planning Relationships: | [5 empty] | Adjacent to WC. Adjacent to changing area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 16 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Suitable for the examination of barrier-nursed patients. Lamp indicator call situated over door outside room. Link to departmental computer management system. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0119
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0119 |  |  |  |  | Imaging room: Ultrasound, general and minor interventional
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | on bed - dimmable
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0119
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0119 |  |  |  |  | Imaging room: Ultrasound, general and minor interventional
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley, wheelchair & equipment access (1500mm); Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Non-essential - Project Option Solar control. Blackout/dimout Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0119
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0119 |  |  |  |  | Imaging room: Ultrasound, general and minor interventional
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO022 |  | HOOK, double, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG053 |  | LUMINAIRE, examination, ceiling, adjustable, 1000 lux | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT004 |  | OUTLET cable, fused, 13 amp, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT461 |  | OUTLET, nitrous oxide, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT480 |  | OUTLET, gas scavenging (AGS), medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC073 |  | CABINET, upper, modular storage, for 600 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW053 |  | WORKTOP, clinical, for 3 x 400 facing modular storage cabinets, 1365W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC001 |  | SWITCH 5amp ac single pole, 1 way, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC031 |  | SWITCH dimmer, fixed position, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRO601 |  | TROUGH scrub-up, hospital pattern, stainless steel, single, 75mm upstand, 800W 450D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WRT068 |  | WORKTOP, non-clinical, 1800W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS006 |  | DISPENSER, disposable nailbrush, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA303 |  | CHAIR, swivel, height adjustable 540-790, tilting back, adjustable footrest, wipeable, 5 star base, on castors/glides | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA363 |  | CHAIR, height adjustable, with arms, high back, swivel, 5 star base, wipeable, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0119
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0119 |  |  |  |  | Imaging room: Ultrasound, general and minor interventional
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | COU010 |  | COUCH, examination/treatment, (3 section), variable height, retractable wheels, with paper roll holder | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CUP418 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 483W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL008 |  | HOLDER, sack with lid foot operated, large, freestanding, 960H 500W 415D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO135 |  | TROLLEY, dressing/equipment, 6 clear trays, buffered, 890H 510W 480D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | ULT017 |  | ULTRASOUND computed sonography, 128 channels, multi purpose, mobile, 1295H 635W 920D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | WAR051 |  | WARMER, ultrasound couplant gel, 200H 100W 150D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0120
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0120 |  |  |  |  | Imaging room: Ultrasound, interventional
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may arrive on foot in a wheelchair or on a trolley 2) Patient may arrive on a trolley or in a bed. 3) Patient is positioned or repositioned for examination. 4) Administration of general anaesthetic. 5) Interventional work or imaging procedure examination. 6) Invasive surgical procedures under ultrasound control, e.g. biopsy. 7) Holding working supplies of sterile items. 8) Preparing and use of sterile trays and packs. 9) Oxygen and vacuum services may be used for resuscitation. 10) Clinical hand washing/scrubbing. 11) Daily holding/sorting of documents, records, radiology films in clinical or diagnostic areas. 12) Holding linen supply. 13) Immediate reporting of ultrasound scanning. 14) Recording patient data/notes. 15) Communicating by a ward or department (Two-way communication system) within and outside hospital (telephone). 16) Using contrast media warmer.
| Personnel: | [6 empty] | 1 x Patient 4 x Staff 1 - 2 trainee staff
| Planning Relationships: | [5 empty] | En-suite WC. Adjacent to changing area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 27 |  |  |  |  | Height (mm): |  |  |  | 3000
| Notes: | [7 empty] | Suitable for the examination of barrier-nursed patients. Lamp indicator call situated over door outside room. Full anaesthesia facilities are provided. Link to departmental computer management system.
| ADB | [7 empty] | Room Environmental Data
E0120
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0120 |  |  |  |  | Imaging room: Ultrasound, interventional
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | on bed - dimmable
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0120
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0120 |  |  |  |  | Imaging room: Ultrasound, interventional
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 3 sets of doors - radiation protection: 2 x personnel, wheelchair & equipment access (1000mm) 1 x personnel, bed, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Non-essential - Project Option Solar control. Blackout/dimout Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0120
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0120 |  |  |  |  | Imaging room: Ultrasound, interventional
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG053 |  | LUMINAIRE, examination, ceiling, adjustable, 1000 lux | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT004 |  | OUTLET cable, fused, 13 amp, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PEN002 |  | PENDANT ANAESTHETIC medical and power supply unit, vertical movement, ceiling mounted, outlets comprising: 4x socket outlet, 13amp, switched, double 1x outlet oxygen, medical 1x outlet nitrous oxide, medical 1x outlet compressed air medical, (4 bar) 1x outlet compressed air surgical, (7 bar) 2x outlet vacuum, medical 1x AGS, medical | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC023 |  | CABINET, upper, modular storage, for 400 facing inserts, with door, 750H | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC121 |  | CATHETER CUPBOARD, 600mm facing, with formed plastic liners, incl. shelf with 5 telescopic rails , 1 door, on plinth, o/a height 2100 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW056 |  | WORKTOP, clinical, for 6 x 400 facing modular storage cabinets, 2730W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC001 |  | SWITCH 5amp ac single pole, 1 way, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC031 |  | SWITCH dimmer, fixed position, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRO601 |  | TROUGH scrub-up, hospital pattern, stainless steel, single, 75mm upstand, 800W 450D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS006 |  | DISPENSER, disposable nailbrush, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | ANA001 |  | ANAESTHETIC MACHINE/WORKSTATION electrically powered piston ventilator, mobile, 1350H 750W 650D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0120
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0120 |  |  |  |  | Imaging room: Ultrasound, interventional
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | KIC001 |  | KICKABOUT, bowl stand, stainless steel, 360mm dia. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STA142 |  | STAND, infusion, twin hook, breaks, mobile | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | STO006 |  | STOOL, surgeon/anaesthetist, height adjustable, includes anti-static seat pads | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB077 |  | TABLE, surgical procedures, radiotranslucen,t o/a 1005H 2100W 835D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO133 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 750W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO135 |  | TROLLEY, dressing/equipment, 6 clear trays, buffered, 890H 510W 480D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | ULT017 |  | ULTRASOUND computed sonography, 128 channels, multi purpose, mobile, 1295H 635W 920D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | WAR051 |  | WARMER, ultrasound couplant gel, 200H 100W 150D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0124
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0124 |  |  |  |  | Imaging room: CR, general x-ray, with chest x-ray With mobile examination lamp, CR in control area No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may arrive on foot in a wheelchair or on a trolley 2) Patient may arrive on a trolley or in a bed. 3) Patient is positioned or repositioned for examination. 4) Radiation protection equipment will be used. 5) Imaging x-ray examination of patient. 6) Imaging plate(s) taken to processing area. 7) Oxygen and vacuum services may be used for resuscitation. 8) Clinical hand washing. 9) Displaying notices. 10) Marker/wall board may be used. 11) Small items of equipment and sundries are stored. 12) Using contrast media warmer.
| Personnel: | [6 empty] | 1 x Patient 2 x Staff
| Planning Relationships: | [5 empty] | Adjacent to Digital Processing/viewing area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 30 |  |  |  |  | Height (mm): |  |  |  | 3100
| Notes: | [7 empty] | CR - Computed Radiography Lamp indicator call situated over door outside room. Lamp indicator Radiation Warning at eye level at outside entrance. In the absence of changing cubicle, privacy screen is required. Radiation protection as required. Lighting control panel(s) depending on specific function of the room giving variable levels of illumination. Socket outlets at two metre intervals on each wall. Link to the GP surgery via the telephone wires.
| ADB | [7 empty] | Room Environmental Data
E0124
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0124 |  |  |  |  | Imaging room: CR, general x-ray, with chest x-ray With mobile examination lamp, CR in control area No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6 |  | No intrusive procedures
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V/Sp
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Non-ionising for rooms with x-ray machines
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0124
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0124 |  |  |  |  | Imaging room: CR, general x-ray, with chest x-ray With mobile examination lamp, CR in control area No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors - radiation protection: 1 x personnel, wheelchair & equipment access (1000mm); 1 x personnel, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0124
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0124 |  |  |  |  | Imaging room: CR, general x-ray, with chest x-ray With mobile examination lamp, CR in control area No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC091 |  | CABINET base, 400mm facing, (400x600 inserts), with formed plastic liners, 1 door hinged right, on plinth, o/a height 900 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC092 |  | CABINET base, 400mm facing, (400x600 inserts), with formed plastic liners, 1 door hinged left, on plinth, o/a height 900 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC096 |  | CABINET base, 400mm facing, (400x600 inserts), with 3 telescopic runners, 1 door hinged left, on plinth, o/a height 900 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSW013 |  | WORKTOP, for 3x 400mm facing inserts cabinets, 1365W 700D nominal | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT059 |  | CONNECTION UNIT switched 13amp, flex, indicator light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLO001 |  | CLOCK battery, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | ILL010 |  | ILLUMINATOR, x-ray film, double, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | RAC196 |  | RACK, x-ray lead apron, 5 hangers hinged, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | XRA010 |  | X-RAY CS, ceiling suspensions, with telescopic tube of column and rotating/tilting arm | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0124
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0124 |  |  |  |  | Imaging room: CR, general x-ray, with chest x-ray With mobile examination lamp, CR in control area No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | XRA021 |  | X-RAY TABLE PATIENT, floating top, motorised variable height horizontal bucky, 800H 2180W 700D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | XRA022 |  | X-RAY CONTROL CONSOLE for generator, freestanding, 870H 470W 360D (Part of IMG028, IMG030 and XRA023) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | XRA023 |  | X-RAY CONTROL CABINET for generator, freestanding, 950H 850W 535D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | XRA024 |  | X-RAY TARNSFORMER CABINET for generator, 65kW with options for 50, 80,100kW, 1950H 590W 570D, (Part of XRA023) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | XRA030 |  | X-RAY CHEST stand, universal, includes Bucky mechanism | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB050 |  | CABINET, x-ray cassette storage, mobile, 550H 700W 500D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA017 |  | CHAIR, upright, upholstered, stacking | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG140 |  | IMAGING, Computed Radiography Unit. In room ID workstation, (Part of IMG141) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG141 |  | IMAGING, Computed Radiography Unit, large high-throughput, CR plate reader, o/a 1720H 730W 720D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAD001 |  | STEP, 3 tread, 4 sprung wheels, 750H 600W 500D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LIG015 |  | LUMINAIRE observation/examination, mobile, 1000 lux | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SCR064 |  | SCREEN, x-ray radiation protection, lead rubber, mobile, 900H 700L, lead equivalent 0.5mm Pb. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO133 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 750W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO310 |  | TROLLEY, emergency/resuscitation, complete with defibrillator, 955H 825W 575D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0128
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0128 |  |  |  |  | Imaging room: conventional, general x-ray with chest and scull x-ray Imaging tube ceiling suspended, CR in control area No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may arrive on foot in a wheelchair or on a trolley 2) Patient may arrive on a trolley or in a bed. 3) Patient is positioned or repositioned for examination. 4) Radiation protection equipment will be used. 5) Imaging x-ray examination of patient. 6) Imaging x-ray examination of patient skull. 7) Imaging plate(s) taken to processing area. 8) Oxygen and vacuum services may be used for resuscitation. 9) Clinical hand washing. 10) Displaying notices. 11) Marker/wall board may be used. 12) Holding equipment manuals. 13) Small items of equipment and sundries are stored. 14) Positioning aids e.g. wedges pillows and other immobilisation devices are stored. 15) Storing of x-ray lead field alignment fittings.
| Personnel: | [6 empty] | 1 x Patient 4 x Staff
| Planning Relationships: | [5 empty] | Adjacent to Digital Processing/viewing area. Close to changing facilities. Close to sub-waiting.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 33 |  |  |  |  | Height (mm): |  |  |  | 3100
| Notes: | [7 empty] | CR - Computed Radiography Lamp indicator call situated over door outside room. Lamp indicator Radiation Warning at eye level at outside entrance. Ancillary items required. Space required for the following, which may be stored elsewhere: Infusion stand, twin hook, mobile (STA142). Examination lamp, mobile (LIG015). Wall mounted telephone handset is required. Radiation protection as required. Lighting control panel(s) depending on specific function of the room giving variable levels of illumination. Socket outlets at two metre intervals on each wall. Link to departmental computer management system. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0128
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0128 |  |  |  |  | Imaging room: conventional, general x-ray with chest and scull x-ray Imaging tube ceiling suspended, CR in control area No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6 |  | No intrusive procedures
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V/Sp
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Non-ionising for rooms with x-ray machines
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0128
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0128 |  |  |  |  | Imaging room: conventional, general x-ray with chest and scull x-ray Imaging tube ceiling suspended, CR in control area No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors - radiation protection: 1 x personnel access (900mm); 1 x personnel, bed, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0128
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0128 |  |  |  |  | Imaging room: conventional, general x-ray with chest and scull x-ray Imaging tube ceiling suspended, CR in control area No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LIG071 |  | ILLUMINATED SIGN 'RADIATION ON', wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 10 |  |  | 10 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT079 |  | OUTLET isolator, equipment manufacturer's specification | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC023 |  | CABINET, upper, modular storage, for 400 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW053 |  | WORKTOP, clinical, for 3 x 400 facing modular storage cabinets, 1365W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC062 |  | EMERGENCY STOP switch button, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SCR063 |  | SCREEN shielding, radiation proof | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | XRA036 |  | X-RAY SCULL , ceiling mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | XRA037 |  | X-RAY GENERATOR CABINET, (Part of XRA036) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | XRA041 |  | X-RAY TABLE - digital | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | XRA043 |  | X-RAY UNIT (tube), with ceiling suspensions track - digital | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | XRA045 |  | X-RAY CHEST stand - digital | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0128
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0128 |  |  |  |  | Imaging room: conventional, general x-ray with chest and scull x-ray Imaging tube ceiling suspended, CR in control area No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | XRA048 |  | X-RAY CONTROL CONSOLE - digital | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | XRA049 |  | X-RAY GENERATOR CABINET | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP011 |  | CUPBOARD, metal, with 4 pull out galvanised shelves, lockable, 1800H 1000W 500D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL020 |  | HOLDER, sharps box, up to 7 litre capacity, rail/trolley hang or wall mounted, 170H 125W 100D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC197 |  | RACK, x-ray lead apron, 6 swivel arms, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT002 |  | TROLLEY, modular storage, single open frame, including handle and worktop, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0133
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0133 |  |  |  |  | Imaging room: extra-oral x-ray with ultrasound, sialographic Dental
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Dental imaging x-ray examination. 2) Ultrasound examination. 3) Small items of equipment and sundries are stored. 4) Clinical hand washing.
| Personnel: | [6 empty] | 1 x Patient Up to 3 staff (practitioner, an operator, a nurse) Up to 3 others (observers or carers)
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 13.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0133
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0133 |  |  |  |  | Imaging room: extra-oral x-ray with ultrasound, sialographic Dental
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6 |  | No intrusive procedures
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V/Sp
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Non-ionising for rooms with x-ray machines
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0133
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0133 |  |  |  |  | Imaging room: extra-oral x-ray with ultrasound, sialographic Dental
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - radiation protection: 1 x personnel, trolley, wheelchair & equipment access (1500mm) Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0133
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0133 |  |  |  |  | Imaging room: extra-oral x-ray with ultrasound, sialographic Dental
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG071 |  | ILLUMINATED SIGN 'RADIATION ON', wall mounted | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC062 |  | EMERGENCY STOP switch button, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WRT012 |  | WORKTOP, non-clinical, 1200W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | XRA003 |  | X-RAY TUBE, dental, with articulating flexible arm, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | XRA004 |  | X-RAY GENERATOR for dental tube, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC197 |  | RACK, x-ray lead apron, 6 swivel arms, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT001 |  | TROLLEY, modular storage, single open frame, including handle, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | ULT017 |  | ULTRASOUND computed sonography, 128 channels, multi purpose, mobile, 1295H 635W 920D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0142
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0142 |  |  |  |  | Imaging room: Mammography with biopsy No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may arrive on foot in a wheelchair or on a trolley 2) Mammography examination. 3) Administration of sedation. 4) Performing lesion aspiration or needle biopsy. 5) Small items of equipment and sundries are stored. 6) Radiation protection equipment will be used. 7) Holding 'SHARPS' in containers for collection/disposal. 8) Clinical hand washing. 9) Oxygen and vacuum services may be used for resuscitation.
| Personnel: | [6 empty] | 1 x Patient 1- 4 Staff (may incl. radiologist, nurse, radiographer, pathologist0
| Planning Relationships: | [5 empty] | Close to consulting/examination room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 17 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Storing attachments and accessories which are necessary in order to provide a full service. Privacy curtain required at access door. Lamp indicator Radiation Warning at eye level at outside entrance. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0142
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0142 |  |  |  |  | Imaging room: Mammography with biopsy No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V/Sp
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Non-ionising for rooms with x-ray machines
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0142
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0142 |  |  |  |  | Imaging room: Mammography with biopsy No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - radiation protection: 1 x personnel, trolley, wheelchair & equipment access (1500mm); Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0142
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0142 |  |  |  |  | Imaging room: Mammography with biopsy No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG058 |  | LUMINAIRE, examination, wall, adjustable, 1000 lux | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC015 |  | CABINET, base, modular storage, for 400 facing inserts, 5 drawers, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW054 |  | WORKTOP, clinical, for 4 x 400 facing modular storage cabinets, 1820W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC033 |  | SWITCH dimmer, 3 position, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC062 |  | EMERGENCY STOP switch button, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG041 |  | IMAGER MAMMOGRAPHY UNIT, with rotation of swivel U-arm, floor mounted | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG042 |  | IMAGER CONTROL CABINET and GENERATOR for mammography, approximate 2000H 1000W 1000D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG043 |  | IMAGER POWER CABINET for mammography, with on/off and emergency off button, (Part of IMG041) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG044 |  | CONTROL CONSOLE and RADIATION PROTECTION SCREEN for mammography unit, (Part of IMG041) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG045 |  | IMAGER MAMMOGRAPHY BIOPSY UNIT | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG109 |  | IMAGING CHAIR, with arms, tilt, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC197 |  | RACK, x-ray lead apron, 6 swivel arms, mobile | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0151
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0151 |  |  |  |  | Imaging room: Bone Mineral Densitometry (BMD)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may arrive on foot in a wheelchair or on a trolley 2) Patient may arrive on a trolley or in a bed. 3) Patient is positioned or repositioned for examination. 4) Radiation protection equipment will be used. 5) X-ray bone densitometry examination of patient. 6) Oxygen and vacuum services may be used for resuscitation. 7) Clinical hand washing. 8) Visual display terminal(s) may be used. 9) Displaying notices. 10) Marker/wall board may be used. 11) Small items of equipment and sundries are stored.
| Personnel: | [6 empty] | 1 x Patient 2 x Staff
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 18 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Lamp indicator Radiation Warning at eye level at outside entrance. Radiation protection as required. Lighting control panel(s) depending on specific function of the room giving variable levels of illumination. Link to the GP surgery via the telephone wires. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0151
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0151 |  |  |  |  | Imaging room: Bone Mineral Densitometry (BMD)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6 |  | No intrusive procedures
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V/Sp
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Non-ionising for rooms with x-ray machines
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0151
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0151 |  |  |  |  | Imaging room: Bone Mineral Densitometry (BMD)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - radiation protection: 1 x personnel, trolley, wheelchair & equipment access (1500mm) Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0151
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0151 |  |  |  |  | Imaging room: Bone Mineral Densitometry (BMD)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW054 |  | WORKTOP, clinical, for 4 x 400 facing modular storage cabinets, 1820W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA363 |  | CHAIR, height adjustable, with arms, high back, swivel, 5 star base, wipeable, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOI003 |  | HOIST PATIENT, chair type, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG055 |  | IMAGER BONE DENSITOMETRY UNIT, with rotating detector/X-ray tube and mowing couch, floor mounted, approximate 1500H 1500W 3000D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG056 |  | IMAGER CONTROL CABINET for bone densitometry, approximate 1500H 750W 750D, (Part of IMG055) | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0162
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0162 |  |  |  |  | Imaging room: Ultrasound, 2 bays With reporting workstation. Access to en suit to WC. Paediatric No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may arrive on foot in a wheelchair or on a trolley 2) Patient may arrive on a trolley or in a bed. 3) Patient is positioned or repositioned for examination. 4) Administration of sedation. 5) Interventional work or imaging procedure examination. 6) Invasive surgical procedures under ultrasound control, e.g. biopsy. 7) Oxygen and vacuum services may be used for resuscitation. 8) Holding working supplies of sterile items. 9) Daily holding/sorting of documents, records, radiology films in clinical or diagnostic areas. 10) Holding linen supply. 11) Clinical hand washing. 12) Immediate reporting of ultrasound scanning. 13) Recording patient data/notes. 14) Visual display terminal(s) may be used. 15) Communicating by a ward or department (Two-way communication system) within and outside hospital (telephone). 16) Using gel warmer.
| Personnel: | [6 empty] | 2 x Patient 3 x Staff 2 x Additional staff intermittently Intermittent use
| Planning Relationships: | [5 empty] | Adjacent to ultrasound waiting/changing. En-suite WC.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 40 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Lamp indicator Radiation Warning at eye level at outside entrance. To occupy the patient during the examination provision of ceiling suspended video monitors, projector, mobiles should be considered. Link to departmental computer management system/PACS.
| ADB | [7 empty] | Room Environmental Data
E0162
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0162 |  |  |  |  | Imaging room: Ultrasound, 2 bays With reporting workstation. Access to en suit to WC. Paediatric No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6 |  | No intrusive procedures
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | on bed - dimmable. 2 way switching at door, monitor and each bed.
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0162
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0162 |  |  |  |  | Imaging room: Ultrasound, 2 bays With reporting workstation. Access to en suit to WC. Paediatric No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 1 x personnel, wheelchair & equipment access (1000mm); 1 x personnel, bed, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Non-essential - Project Option Solar control. Blackout/dimout Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0162
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0162 |  |  |  |  | Imaging room: Ultrasound, 2 bays With reporting workstation. Access to en suit to WC. Paediatric No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO005 |  | CLOCK impulse, wall mounted | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO022 |  | HOOK, double, wall mounted | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LIG058 |  | LUMINAIRE, examination, wall, adjustable, 1000 lux | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | MSC186 |  | CABINET base, 400mm facing, with 2 shelves, open, on plinth, o/a height 900 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC187 |  | CABINET base, 400mm facing, with 2 shelves, 1 door hinged right, on plinth, o/a height 900 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC263 |  | CABINET/DRAWER features, base, 400mm facing, 4 drawer, on plinth, o/a height 900 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSW014 |  | WORKTOP, for 4x 400mm facing inserts cabinets, 1820W 700D nominal | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT210 |  | SOCKET outlet two-way communication system (intercom). | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PIG016 |  | PIGEONHOLE UNIT, two level, 12 compartments, wall mounted, 800H 1000W 450D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SHE241 |  | SHELF, 1800W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | STF156 |  | STORAGE UNIT, lower, 3 drawer, 350H 600W 450D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | STF274 |  | STORAGE UNIT, upper, cupboard, 2 door, 1 shelf, 550H 600W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC031 |  | SWITCH dimmer, fixed position, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TRA026 |  | TRACK, curtain, three sided, U-shape, 2700L 1800W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WKT133 |  | WORKTOP, cantilevered from wall, 2500W 550D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0162
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0162 |  |  |  |  | Imaging room: Ultrasound, 2 bays With reporting workstation. Access to en suit to WC. Paediatric No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | ILL010 |  | ILLUMINATOR, x-ray film, double, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | RAC120 |  | RACK, film cassette, wall mounted, 375H 450W 75D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA017 |  | CHAIR, upright, upholstered, stacking | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA063 |  | CHAIR, height adjustable, with arms, high back, swivel, 5 star base, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COU010 |  | COUCH, examination/treatment, (3 section), variable height, retractable wheels, with paper roll holder | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | ULT017 |  | ULTRASOUND computed sonography, 128 channels, multi purpose, mobile, 1295H 635W 920D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | WAR051 |  | WARMER, ultrasound couplant gel, 200H 100W 150D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0163
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0163 |  |  |  |  | Imaging room: Ultrasound, 3 mixed bays With reporting workstation. Access to en suit to WC. Paediatric No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may arrive on foot in a wheelchair or on a trolley 2) Patient may arrive on a trolley or in a bed. 3) Patient is positioned or repositioned for examination. 4) Administration of sedation. 5) Interventional work or imaging procedure examination. 6) Invasive surgical procedures under ultrasound control, e.g. biopsy. 7) Oxygen and vacuum services may be used for resuscitation. 8) Holding working supplies of sterile items. 9) Clinical hand washing. 10) Daily holding/sorting of documents, records, radiology films in clinical or diagnostic areas. 11) Holding linen supply. 12) Immediate reporting of ultrasound scanning. 13) Recording patient data/notes. 14) Visual display terminal(s) may be used. 15) Communicating by a ward or department (Two-way communication system) within and outside hospital (telephone).
| Personnel: | [6 empty] | 3 x Patient 4 x Staff 2 x Additional staff intermittently Intermittent use
| Planning Relationships: | [5 empty] | Adjacent to ultrasound waiting/changing. En-suite WC.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 50 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Lamp indicator Radiation Warning at eye level at outside entrance. To occupy the patient during the examination provision of ceiling suspended video monitors, projector, mobiles should be considered. Link to departmental computer management system. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0163
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0163 |  |  |  |  | Imaging room: Ultrasound, 3 mixed bays With reporting workstation. Access to en suit to WC. Paediatric No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6 |  | No intrusive procedures
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | on bed - dimmable. 2 way switching at door, monitor and each bed.
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0163
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0163 |  |  |  |  | Imaging room: Ultrasound, 3 mixed bays With reporting workstation. Access to en suit to WC. Paediatric No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 1 x personnel, wheelchair & equipment access (1000mm); 1 x personnel, bed, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Non-essential - Project Option Solar control. Blackout/dimout Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0163
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0163 |  |  |  |  | Imaging room: Ultrasound, 3 mixed bays With reporting workstation. Access to en suit to WC. Paediatric No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO005 |  | CLOCK impulse, wall mounted | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO022 |  | HOOK, double, wall mounted | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | LIG058 |  | LUMINAIRE, examination, wall, adjustable, 1000 lux | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 11 |  |  | 11 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SHE241 |  | SHELF, 1800W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC011 |  | CABINET, base, modular storage, for 400 facing inserts, open, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC016 |  | CABINET, base, modular storage, for 400 facing inserts, 4 drawers, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC073 |  | CABINET, upper, modular storage, for 600 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW054 |  | WORKTOP, clinical, for 4 x 400 facing modular storage cabinets, 1820W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | STF156 |  | STORAGE UNIT, lower, 3 drawer, 350H 600W 450D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC031 |  | SWITCH dimmer, fixed position, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TRA028 |  | TRACK, curtain, three sided, U-shape, 2700L 2400W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRA133 |  | TRACK, curtain, two sided, L-shape, 2700L 2100W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WKT133 |  | WORKTOP, cantilevered from wall, 2500W 550D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 3 |  |  | 3 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0163
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0163 |  |  |  |  | Imaging room: Ultrasound, 3 mixed bays With reporting workstation. Access to en suit to WC. Paediatric No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 3 |  |  | 3 |  |  |  |  | CHA303 |  | CHAIR, swivel, height adjustable 540-790, tilting back, adjustable footrest, wipeable, 5 star base, on castors/glides | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA363 |  | CHAIR, height adjustable, with arms, high back, swivel, 5 star base, wipeable, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COU010 |  | COUCH, examination/treatment, (3 section), variable height, retractable wheels, with paper roll holder | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | TRO135 |  | TROLLEY, dressing/equipment, 6 clear trays, buffered, 890H 510W 480D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | ULT017 |  | ULTRASOUND computed sonography, 128 channels, multi purpose, mobile, 1295H 635W 920D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | WAR051 |  | WARMER, ultrasound couplant gel, 200H 100W 150D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0181
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0181 |  |  |  |  | Imaging room: mammography
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Mammography examination. 2) Small items of equipment and sundries are stored. 3) Radiation protection equipment will be used. 4) Clinical hand washing. 5) Patient may be ambulant with/without walking aids, in a wheelchair or requiring assistance. 6) Patient may undress/dress in privacy. 7) Computer workstation(s) may be used. 8) Electronic patient records (EPRs) may be accessed and updated. 9) Medical hand sanitizer may be used.
| Personnel: | [6 empty] | 1 x Patient 1 x Staff
| Planning Relationships: | [5 empty] | Close to consulting/examination room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 16 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Medical oxygen & vacuum outlets - project team option. Lamp indicator Radiation Warning at eye level at outside entrance. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0181
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0181 |  |  |  |  | Imaging room: mammography
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V/Sp
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Non-ionising for rooms with x-ray machines
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0181
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0181 |  |  |  |  | Imaging room: mammography
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - radiation protection: 1 x personnel, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0181
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0181 |  |  |  |  | Imaging room: mammography
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG071 |  | ILLUMINATED SIGN 'RADIATION ON', wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW072 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 1200W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC062 |  | EMERGENCY STOP switch button, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRA172 |  | TRACK, curtain, one sided, 3800L | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA304 |  | CHAIR, swivel, height adjustable, medium back, wipeable, 5 star base, on glides | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG047 |  | IMAGER DIGITAL MAMMOGRAPHY UNIT, floor mounted with rotation of swive arm, floor mounted | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG048 |  | IMAGER CONTROL CONSOLE and RADIATION PROTECTION SCREEN with GENERATOR for mammography unit (part of IMG047) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG109 |  | IMAGING CHAIR, with arms, tilt, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC197 |  | RACK, x-ray lead apron, 6 swivel arms, mobile | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0303
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0303 |  |  |  |  | Imaging room: universal fluoroscopy, barium Incl. general imaging and chest bucky No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may arrive on foot in a wheelchair or on a trolley 2) Patient may arrive on a trolley or in a bed. 3) Patient to take barium contrast media. 4) Patient is positioned or repositioned for examination. 5) Fluoroscopy examination of patient. 6) Radiation protection equipment will be used. 7) Clinical hand washing. 8) Oxygen and vacuum services may be used for resuscitation. 9) Recording patient data/notes. 10) Displaying notices. 11) Marker/wall board may be used. 12) Small items of equipment and sundries are stored. 13) Clinical hand washing. 14) Using contrast media warmer/mixer.
| Personnel: | [6 empty] | 1 x Patient 5 x Staff
| Planning Relationships: | [5 empty] | Adjacent to Processing area. Close to changing facilities. Close to sub-waiting. Close to recovery room/area. Easy access to WC.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 39 |  |  |  |  | Height (mm): |  |  |  | 3100
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Lamp indicator Radiation Warning at eye level at outside entrance. General imaging and chest bucky not required for fluoroscopy/fluorography may be install as back up the facilities in other general imaging room - project team option. Diagnostic Investigations using an images intensifier will usually be carried out in conjunction with contrast media for a range of investigations. If clinical procedure using Endoscopes or Gastroscopes are conducted in this suite then additional space should be allocated for Endoscopy trolleys. These procedure do not involve the use of barium contrast. Additional equipment notes: Wall mounted telephone handset is required. Radiation protection including warning light at entrances. Outlets 13A (OUT010) at two metre intervals on each wall. Lighting control panel(s) for variable illumination. Wireway for link to departmental computer management system/PACS. 'Do Not Enter' signals outside each door. Radiology screen, Infusion stand and Lamp examination mobile may be stored elsewhere. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0303
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0303 |  |  |  |  | Imaging room: universal fluoroscopy, barium Incl. general imaging and chest bucky No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Non-ionising for rooms with x-ray machines
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0303
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0303 |  |  |  |  | Imaging room: universal fluoroscopy, barium Incl. general imaging and chest bucky No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 3 sets of doors - radiation protection: 2 x personnel, wheelchair & equipment access (1000mm) 1 x personnel, bed, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0303
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0303 |  |  |  |  | Imaging room: universal fluoroscopy, barium Incl. general imaging and chest bucky No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | IMG025 |  | IMAGE INTENSIFIER and X-RAY TUBE FLUOROSCOPY, U-arm, floor mounted, (intensifier above table, x-ray tube below) | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT207 |  | SOCKET outlet aerial television, closed circuit (CCTV) | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW053 |  | WORKTOP, clinical, for 3 x 400 facing modular storage cabinets, 1365W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG116 |  | IMAGE GENERATOR/POWER DISTRIBUTION CABINET, (Part of fluoroscopy imager) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SCR061 |  | SCREEN shielding, radiation proof, 2mm lead, solid/glass, 2000H 2100L, angle | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | XRA010 |  | X-RAY CS, ceiling suspensions, with telescopic tube of column and rotating/tilting arm | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | XRA018 |  | X-RAY CS RAIL, ceiling suspensions, 2455mm (3655 w/optional extenstion rail) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | XRA030 |  | X-RAY CHEST stand, universal, includes Bucky mechanism | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0303
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0303 |  |  |  |  | Imaging room: universal fluoroscopy, barium Incl. general imaging and chest bucky No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CHA063 |  | CHAIR, height adjustable, with arms, high back, swivel, 5 star base, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP011 |  | CUPBOARD, metal, with 4 pull out galvanised shelves, lockable, 1800H 1000W 500D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DES006 |  | DESK, cantilever, single pedestal 3 drawer, modesty panel, 1200W 750D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | IMG102 |  | MONITOR viewing flat panel display for image intensifier, (Part of IMG025, IMG026, IMG028 and IMG030) | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | IMG104 |  | TROLLEY for monitor image intensifier, (Part of IMG102) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG105 |  | TABLE PATIENT - image intensifier, X-ray, floating top, (Part of IMG026, or IMG030) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAD001 |  | STEP, 3 tread, 4 sprung wheels, 750H 600W 500D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT001 |  | TROLLEY, modular storage, single open frame, including handle, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STO007 |  | STOOL, metal frame, upholstered, 710 height | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO135 |  | TROLLEY, dressing/equipment, 6 clear trays, buffered, 890H 510W 480D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0305
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0305 |  |  |  |  | Imaging room: remote fluoroscopy, barium No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may arrive on foot in a wheelchair or on a trolley 2) Patient may arrive on a trolley or in a bed. 3) Patient to take barium contrast media. 4) Patient is positioned or repositioned for examination. 5) Fluoroscopy examination of patient. 6) Radiation protection equipment will be used. 7) Oxygen and vacuum services may be used for resuscitation. 8) Clinical hand washing. 9) Recording patient data/notes. 10) Displaying notices. 11) Marker/wall board may be used. 12) Small items of equipment and sundries are stored. 13) Using contrast media warmer/mixer.
| Personnel: | [6 empty] | 1 x Patient 5 x Staff
| Planning Relationships: | [5 empty] | Adjacent to Processing area. Close to changing facilities. Close to sub-waiting. Close to recovery room/area. Easy access to WC.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 39 |  |  |  |  | Height (mm): |  |  |  | 3100
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Lamp indicator Radiation Warning at eye level at outside entrance. Diagnostic Investigations using an images intensifier will usually be carried out in conjunction with contrast media for a range of investigations. If clinical procedure using Endoscopes or Gastroscopes are conducted in this suite then additional space should be allocated for Endoscopy trolleys. These procedure do not involve the use of barium contrast. Additional equipment notes: X-ray chest bucky - project team option. Radiology screen, Infusion stand and Lamp examination mobile may be stored elsewhere. Wall mounted telephone handset is required. Radiation protection including Room Warning Light. Outlets 13A (OUT010) at two metre intervals on each wall. 'Do Not Enter' signals outside each door. Lighting control panel(s) for variable illumination. Wireway for link to departmental computer management system/PACS. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0305
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0305 |  |  |  |  | Imaging room: remote fluoroscopy, barium No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Non-ionising for rooms with x-ray machines
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0305
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0305 |  |  |  |  | Imaging room: remote fluoroscopy, barium No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 3 sets of doors - radiation protection: 2 x personnel, wheelchair & equipment access (1000mm) 1 x personnel, bed, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0305
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0305 |  |  |  |  | Imaging room: remote fluoroscopy, barium No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | IMG026 |  | IMAGE INTENSIFIER and X-RAY TUBE FLUOROSCOPY, U-arm, floor mounted, (intensifier underneath the table, x-ray tube above) | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT207 |  | SOCKET outlet aerial television, closed circuit (CCTV) | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW053 |  | WORKTOP, clinical, for 3 x 400 facing modular storage cabinets, 1365W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG116 |  | IMAGE GENERATOR/POWER DISTRIBUTION CABINET, (Part of fluoroscopy imager) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SCR062 |  | SCREEN shielding, radiation proof, 2mm lead, solid/glass, 2000H 5100L, angle | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA363 |  | CHAIR, height adjustable, with arms, high back, swivel, 5 star base, wipeable, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP011 |  | CUPBOARD, metal, with 4 pull out galvanised shelves, lockable, 1800H 1000W 500D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0305
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0305 |  |  |  |  | Imaging room: remote fluoroscopy, barium No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | DES006 |  | DESK, cantilever, single pedestal 3 drawer, modesty panel, 1200W 750D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | IMG102 |  | MONITOR viewing flat panel display for image intensifier, (Part of IMG025, IMG026, IMG028 and IMG030) | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | IMG104 |  | TROLLEY for monitor image intensifier, (Part of IMG102) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG105 |  | TABLE PATIENT - image intensifier, X-ray, floating top, (Part of IMG026, or IMG030) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAD001 |  | STEP, 3 tread, 4 sprung wheels, 750H 600W 500D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT001 |  | TROLLEY, modular storage, single open frame, including handle, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STO007 |  | STOOL, metal frame, upholstered, 710 height | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO135 |  | TROLLEY, dressing/equipment, 6 clear trays, buffered, 890H 510W 480D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0307
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0307 |  |  |  |  | Imaging room: fluoroscopy, non-vascular interventional No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may arrive on foot in a wheelchair or on a trolley 2) Patient may arrive on a trolley or in a bed. 3) Patient is positioned or repositioned for examination. 4) Fluoroscopy examination of patient. 5) Non-vascular imaging procedure, (may incl. barium). 6) Radiation protection equipment will be used. 7) Oxygen and vacuum services may be used for resuscitation. 8) Clinical hand washing. 9) Recording patient data/notes. 10) Displaying notices. 11) Marker/wall board may be used. 12) Small items of equipment and sundries are stored. 13) Using contrast media warmer/mixer.
| Personnel: | [6 empty] | 1 x Patient Up to 5 x Staff, (2 radiologists 1-2 radiographers, 1 nurse).
| Planning Relationships: | [5 empty] | Adjacent to Processing area. Close to changing facilities. Close to sub-waiting. Close to recovery room/area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 45 |  |  |  |  | Height (mm): |  |  |  | 3100
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Lamp indicator Radiation Warning at eye level at outside entrance. Provision of facility such as taped music should be considered. Use of hoist may be required. In the majority of circumstances patients, except paediatric, only small number of patients will require general anaesthesia. Anaesthetic gases may be piped, or alternatively provided by mobile cylinder. Radiology screen, Infusion stand and Lamp examination mobile may be stored elsewhere. Wall mounted telephone handset is required. Radiation protection. Outlets 13A (OUT010) at two metre intervals on each wall. Lighting control panel(s) for variable illumination. Wireway for link to departmental computer management system. 'Do Not Enter' signals outside each door. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0307
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0307 |  |  |  |  | Imaging room: fluoroscopy, non-vascular interventional No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Non-ionising for rooms with x-ray machines
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0307
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0307 |  |  |  |  | Imaging room: fluoroscopy, non-vascular interventional No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors - radiation protection: 1 x personnel access (900mm); 1 x personnel, bed, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Essential Radiation proof glazing to control room Roller blind on cath. lab. room side Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0307
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0307 |  |  |  |  | Imaging room: fluoroscopy, non-vascular interventional No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | IMG028 |  | IMAGE INTENSIFIER and X-RAY TUBE FLUOROSCOPY, C-arm, multi-angular, cantilevered | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG050 |  | LUMINAIRE operating (minor) | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW053 |  | WORKTOP, clinical, for 3 x 400 facing modular storage cabinets, 1365W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WRT024 |  | WORKTOP, non-clinical, 2400W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG107 |  | TABLE/TROLLEY, imaging whole-body, 820H 2270W 860D, (Part of IMG028) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG116 |  | IMAGE GENERATOR/POWER DISTRIBUTION CABINET, (Part of fluoroscopy imager) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG121 |  | IMAGE CS RAIL, ceiling suspensions for monitors | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SCR062 |  | SCREEN shielding, radiation proof, 2mm lead, solid/glass, 2000H 5100L, angle | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA363 |  | CHAIR, height adjustable, with arms, high back, swivel, 5 star base, wipeable, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0307
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0307 |  |  |  |  | Imaging room: fluoroscopy, non-vascular interventional No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CUP011 |  | CUPBOARD, metal, with 4 pull out galvanised shelves, lockable, 1800H 1000W 500D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DES006 |  | DESK, cantilever, single pedestal 3 drawer, modesty panel, 1200W 750D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | IMG101 |  | MONITOR viewing, flat panel display for image intensifier, ceiling mounted | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | IMG102 |  | MONITOR viewing flat panel display for image intensifier, (Part of IMG025, IMG026, IMG028 and IMG030) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAD001 |  | STEP, 3 tread, 4 sprung wheels, 750H 600W 500D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT001 |  | TROLLEY, modular storage, single open frame, including handle, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STO007 |  | STOOL, metal frame, upholstered, 710 height | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0311
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0311 |  |  |  |  | Imaging room: fluoroscopy, vascular, angiography No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Using contrast media warmer/mixer. 2) Patient may arrive on a trolley or in a bed. 3) Patient is positioned or repositioned for examination. 4) Fluoroscopy examination of patient. 5) Contrast media may be administered. 6) Patient may have an ultrasound scan. 7) Radiation protection equipment will be used. 8) Oxygen and vacuum services may be used for resuscitation. 9) Clinical hand washing. 10) Displaying notices. 11) Marker/wall board may be used. 12) Small items of equipment and sundries are stored. 13) Resuscitation trolley and associated equipment may be used. 14) Reviewing, archiving and distribution of digital images.
| Personnel: | [6 empty] | 1 x Patient Up to 6 Staff, (2 radiologists, 2 nurses, 2 radiographers).
| Planning Relationships: | [5 empty] | Close to clean utility. Close to changing facilities. Close to sub-waiting. Close to holding/recovery bay. En-suite Anaesthetic Bay and Special Procedures Changing Room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 45 |  |  |  |  | Height (mm): |  |  |  | 3100
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Lamp indicator Radiation Warning at eye level at outside entrance. Power/generator cabinets will possibly be located in adjacent machine room. The contrast media used in the majority of vascular imaging and interventional procedures is an Iodine compound, in aqueous form. Injected via catheter to the specific anatomical location. Additional equipment notes: Provision of facility such as taped music should be considered. Space required for the following, which may be stored elsewhere: Radiography screen, lead rubber, mobile, (SCR064). Infusion stand, twin hook, mobile, (STA142). Resuscitation trolley, (TRO310). Link to departmental computer management system/PACS. Telephone wall mounted is required. Radiation protection as required including room warning lights at all entrances. Purpose made lighting control panel depending on specific function of room giving variable levels of illumination. 'Do Not Enter' sign outside each door.
| ADB | [7 empty] | Room Environmental Data
E0311
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0311 |  |  |  |  | Imaging room: fluoroscopy, vascular, angiography No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Non-ionising for rooms with x-ray machines
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0311
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0311 |  |  |  |  | Imaging room: fluoroscopy, vascular, angiography No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors - radiation protection: 1 x personnel access (900mm); 1 x personnel, bed, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Essential Radiation proof glazing to control room Roller blind on cath. lab. room side Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0311
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0311 |  |  |  |  | Imaging room: fluoroscopy, vascular, angiography No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | IMG030 |  | IMAGE INTENSIFIER and X-RAY TUBE FLUOROSCOPY, C-arm, multi-angular, movable floor mounted l-arm. Includes digital subtraction for angiography | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT050 |  | OUTLET, controlled drugs cupboard | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT056 |  | CONNECTION UNIT, unswitched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT207 |  | SOCKET outlet aerial television, closed circuit (CCTV) | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT461 |  | OUTLET, nitrous oxide, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT480 |  | OUTLET, gas scavenging (AGS), medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMW053 |  | WORKTOP, clinical, for 3 x 400 facing modular storage cabinets, 1365W 700D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB064 |  | CABINET, metal, controlled drugs, 1 door, lockable, with warning light, wall mounted, 550H 600W 300D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG116 |  | IMAGE GENERATOR/POWER DISTRIBUTION CABINET, (Part of fluoroscopy imager) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG121 |  | IMAGE CS RAIL, ceiling suspensions for monitors | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0311
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0311 |  |  |  |  | Imaging room: fluoroscopy, vascular, angiography No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | IMG131 |  | SHIELD lead acrylic, overhead suspended on bracket, 760W 610D lead equivalent 0.5mm Pb, ceiling mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SCR062 |  | SCREEN shielding, radiation proof, 2mm lead, solid/glass, 2000H 5100L, angle | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | ANA001 |  | ANAESTHETIC MACHINE/WORKSTATION electrically powered piston ventilator, mobile, 1350H 750W 650D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP011 |  | CUPBOARD, metal, with 4 pull out galvanised shelves, lockable, 1800H 1000W 500D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | IMG101 |  | MONITOR viewing, flat panel display for image intensifier, ceiling mounted | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG105 |  | TABLE PATIENT - image intensifier, X-ray, floating top, (Part of IMG026, or IMG030) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG136 |  | SHIELD lead acrylic window, over table, height adjustable, mobile, lead equivalent 0.5mm Pb throughout | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAD001 |  | STEP, 3 tread, 4 sprung wheels, 750H 600W 500D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC360 |  | RACK, catheter and guide wire storage, rotary, mobile, wire basket, top 600x600mm, 800mm dia. 230H 600W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STO002 |  | STOOL, height adjustable, 380H 480 dia. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SUC005 |  | SUCTION UNIT, electric, mobile, 845H 470W 410D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SYR001 |  | SYRINGE INJECTOR, automatic, hi pressure injection, contrast media | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO133 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 750W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO201 |  | TROLLEY, instruments, stainless steel, buffered, 870H 920W 620D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0512
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0512 |  |  |  |  | Imaging records room: sorting, collating, despatch No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Receiving and holding new/old films and documents. 2) Sorting and collating x-ray films and documents. 3) Sorting films 4) Obtaining previous films from current or archival film store. 5) Despatching x-ray films and/or reports. 6) Dealing with enquiries relating to the location of films. 7) Holding x-ray films. 8) Withdrawing and refilling films and records. 9) Computer workstation(s) may be used. 10) Printer may be used. 11) Manoeuvring mobile x-ray film trolley.
| Personnel: | [6 empty] | 3 x Staff Intermittent use All day use
| Planning Relationships: | [5 empty] | Close to Reception. Close to offices/reporting area. Close to Data/records/film storage area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 20 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Link to departmental computer management system.
| ADB | [7 empty] | Room Environmental Data
E0512
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0512 |  |  |  |  | Imaging records room: sorting, collating, despatch No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 20
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200 |  | on floor level
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 300 |  | at desk level
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0512
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0512 |  |  |  |  | Imaging records room: sorting, collating, despatch No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear. Solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0512
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0512 |  |  |  |  | Imaging records room: sorting, collating, despatch No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | DRA062 |  | DRAWER UNIT, under worktop, 4 drawer, cut-out to front for film envelopes, 550H 600W 450D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | DRA064 |  | DRAWER UNIT, under worktop, 6 drawer, cut-out to front for film envelopes, 550H 600W 450D | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT059 |  | CONNECTION UNIT switched 13amp, flex, indicator light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | STF127 |  | STORAGE UNIT, lower, cupboard, 2 door, 1 shelf, 550H 600W 450D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WOR074 |  | WORKTOP, 2400W 900D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WOR078 |  | WORKTOP, 3000W 900D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO001 |  | CLOCK battery, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | ILL004 |  | ILLUMINATOR, x-ray film, single, recessed into bench top | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | ILL010 |  | ILLUMINATOR, x-ray film, double, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | RAC355 |  | RACK, x-ray films, 3 position, 300H 1500W 400D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | RAC357 |  | RACK, x-ray films, vertical division, 300H 1200W 450D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP011 |  | CUPBOARD, metal, with 4 pull out galvanised shelves, lockable, 1800H 1000W 500D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DIS037 |  | DISPENSER, sticking tape, ten section, worktop mounted, 170H 900W 330D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | RAC206 |  | RACK, x-ray films, 5tier, 2100H 900W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STO007 |  | STOOL, metal frame, upholstered, 710 height | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STO008 |  | STOOL, kick, retractable castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB005 |  | TABLE, 710H 900W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO114 |  | TROLLEY, documents/library, x-ray film transport | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0514
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0514 |  |  |  |  | Imaging records room: sorting, collating, despatch
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Receiving and holding new/old films and documents. 2) Sorting and collating x-ray films and documents. 3) Sorting films 4) Obtaining previous films from current or archival film store. 5) Despatching x-ray films and/or reports. 6) Dealing with enquiries relating to the location of films. 7) Holding x-ray films. 8) Withdrawing and refilling films and records. 9) Computer workstation(s) may be used. 10) Printer may be used. 11) Manoeuvring mobile x-ray film trolley.
| Personnel: | [6 empty] | 3x Staff Intermittent use All day use
| Planning Relationships: | [5 empty] | Close to Reception. Close to offices/reporting area. Close to Data/records/film storage area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 30 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Link to departmental computer management system.
| ADB | [7 empty] | Room Environmental Data
E0514
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0514 |  |  |  |  | Imaging records room: sorting, collating, despatch
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 20
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200 |  | on floor level
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 300 |  | at desk level
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0514
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0514 |  |  |  |  | Imaging records room: sorting, collating, despatch
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear. Solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0514
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0514 |  |  |  |  | Imaging records room: sorting, collating, despatch
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 4 |  |  | 4 |  |  |  |  | DRA062 |  | DRAWER UNIT, under worktop, 4 drawer, cut-out to front for film envelopes, 550H 600W 450D | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | DRA064 |  | DRAWER UNIT, under worktop, 6 drawer, cut-out to front for film envelopes, 550H 600W 450D | [16 empty] | 1
| 7 |  |  | 7 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT059 |  | CONNECTION UNIT switched 13amp, flex, indicator light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | STF127 |  | STORAGE UNIT, lower, cupboard, 2 door, 1 shelf, 550H 600W 450D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | WOR074 |  | WORKTOP, 2400W 900D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | WOR078 |  | WORKTOP, 3000W 900D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO001 |  | CLOCK battery, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | ILL004 |  | ILLUMINATOR, x-ray film, single, recessed into bench top | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | ILL010 |  | ILLUMINATOR, x-ray film, double, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | RAC355 |  | RACK, x-ray films, 3 position, 300H 1500W 400D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | RAC357 |  | RACK, x-ray films, vertical division, 300H 1200W 450D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP011 |  | CUPBOARD, metal, with 4 pull out galvanised shelves, lockable, 1800H 1000W 500D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DIS037 |  | DISPENSER, sticking tape, ten section, worktop mounted, 170H 900W 330D | [16 empty] | 3
| 60 |  |  | 60 |  |  |  |  | RAC206 |  | RACK, x-ray films, 5tier, 2100H 900W 450D | [16 empty] | 3
| 5 |  |  | 5 |  |  |  |  | STO007 |  | STOOL, metal frame, upholstered, 710 height | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | STO008 |  | STOOL, kick, retractable castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TAB005 |  | TABLE, 710H 900W 600D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | TRO114 |  | TROLLEY, documents/library, x-ray film transport | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0525
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0525 |  |  |  |  | Daylight processing: laser print
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Processing films using dry laser printer to produce hard copies. 2) Maintaining printing equipment.
| Personnel: | [6 empty] | 1 x Person Intermittent use
| Planning Relationships: | [5 empty] | Adjacent to CT scanner room and plant room. Good access from CT Control room. In HBN06/1: Good access from MRI Control room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Electrical supply as appropriate.
| ADB | [7 empty] | Room Environmental Data
E0525
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0525 |  |  |  |  | Daylight processing: laser print
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Minimal fresh air requirement, cooling may be required, system design dictated by equipment requirements.
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Provide by ceiling mounted luminaires with a luminance limiting angle of 65o
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0525
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0525 |  |  |  |  | Daylight processing: laser print
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0525
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0525 |  |  |  |  | Daylight processing: laser print
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PRO016 |  | PROCESSOR, dry laser imager, throughput 150 films per hour, floor standing | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0601
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0601 |  |  |  |  | Scanner room: Computed Tomography (CT) Modified, Room layout in preparation
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may arrive on foot in a wheelchair or on a trolley 2) Patient may arrive on a trolley or in a bed. 3) Positioning/repositioning patient on the scanner table/couch. 4) Contrast media, I.V. injections and other sterile procedures may be prepared. 5) Contrast media may be administered. 6) Patient undergoes scanning with constant aural/visual contact - including when patient is on far side of CT Scanner gantry. 7) Performing lesion aspiration or needle biopsy. 8) Radiation protection equipment will be used. 9) Emergency resuscitation may take place. 10) Oxygen and vacuum services may be used for resuscitation. 11) Clinical hand washing. 12) Small items of equipment and sundries are stored. 13) Disposable items are stored. 14) Using contrast media warmer/mixer. 15) Administration of general anaesthetic.
| Personnel: | [6 empty] | 1 x Patient 4 x Staff Intermittent use
| Planning Relationships: | [5 empty] | Adjacent to Control room with visual contact/aural contact/direct access. Close to sub-waiting. Adjacent to WC.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 36 |  |  |  |  | Height (mm): |  |  |  | 3100
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Ancillary items required. Scanning apparatus selected and positioned as required. Space required for the following, which may be stored elsewhere: Infusion stand, twin hook, mobile, (STA142). Examination lamp, mobile, (LIG015). Anaesthesia unit, (ANA004). Telephone wall mounted is required. Link to departmental computer management system/PACS. Radiation protection as required//including warning light. Lighting control panel giving variable levels of illumination. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0601
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0601 |  |  |  |  | Scanner room: Computed Tomography (CT) Modified, Room layout in preparation
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10 |  | Although non-intrusive, higher air change rate for infection control as patients with lowered immuned system may use the CT
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Minimal fresh air requirement, system design dictated by equipment requirements.
LIGHTING
| Type Of Control: | [13 empty] | V
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0601
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0601 |  |  |  |  | Scanner room: Computed Tomography (CT) Modified, Room layout in preparation
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors - radiation protection: 1 x personnel access (900mm); 1 x personnel, bed, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Essential Radiation proof glazing to control room Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0601
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0601 |  |  |  |  | Scanner room: Computed Tomography (CT) Modified, Room layout in preparation
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL008 |  | PUSH BUTTON staff crash call, reset and integral/adjacent indicator lamp, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | IMG061 |  | IMAGER, COMPUTER TOMOGRAPHY (CT). | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | IMG066 |  | TABLE PATIENT - CT imager, floating top, (Part of IMG061) | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT050 |  | OUTLET, controlled drugs cupboard | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT056 |  | CONNECTION UNIT, unswitched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT207 |  | SOCKET outlet aerial television, closed circuit (CCTV) | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT480 |  | OUTLET, gas scavenging (AGS), medical | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC063 |  | CABINET, base, modular storage, for 600 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC066 |  | CABINET, base, modular storage, for 600 facing inserts, with 4 drawers, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW004 |  | WORKTOP, clinical, for 4 x 600 facing modular storage cabinet, 2620W 500D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | STF286 |  | STORAGE UNIT, upper, cupboard, medicine, 2 door, lockable, 550H 600W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC031 |  | SWITCH dimmer, fixed position, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB034 |  | CABINET warming, contrast media, stainless steel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB064 |  | CABINET, metal, controlled drugs, 1 door, lockable, with warning light, wall mounted, 550H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0601
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0601 |  |  |  |  | Scanner room: Computed Tomography (CT) Modified, Room layout in preparation
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF091 |  | REFRIGERATOR, drug, capacity 35 litre, external temperature gauge, lockable, wall mounted, 510H 380W 445D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL004 |  | HOLDER, sack, with lid foot operated, small, freestanding | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC197 |  | RACK, x-ray lead apron, 6 swivel arms, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT001 |  | TROLLEY, modular storage, single open frame, including handle, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SYR001 |  | SYRINGE INJECTOR, automatic, hi pressure injection, contrast media | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO133 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 750W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0604
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0604 |  |  |  |  | Control room: serving CT room No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Using the operating console to control each scan and monitor the VDT image. 2) Communicating with patient via two-way communication system. 3) X-ray films may be viewed. 4) Retrieving and archiving stored data. 5) Producing hard copy of selected CT images. 6) Communication with colleagues/offices/departments may occur by telephone. 7) Reference books and notices are studied. 8) Small items of equipment and sundries are stored. 9) Stationery/paper is stored. 10) Writing notes.
| Personnel: | [6 empty] | 3 x Staff With intermittent visitors.
| Planning Relationships: | [5 empty] | Adjacent to C.T. scanner room with visual/aural contact & direct access. Convenient to C.T. reporting room. Direct access to C.T. suite corridor.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 16 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | CT Operating console, data storage and hard copy unit - project team option. Good visual & voice contact with the CT scanner room. Activity note: Receiving colleagues/visitors for training/observation of C.T. session. Additional equipment notes: Direct wireway to CT scanner and diagnostic console positions. Link to departmental computer management system/PACS. Radiation protection as required, including room warning light at entrance to Scanner Room. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0604
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0604 |  |  |  |  | Control room: serving CT room No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Minimal fresh air requirement, cooling may be required, system design dictated by equipment requirements.
LIGHTING
| Type Of Control: | [13 empty] | V
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0604
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0604 |  |  |  |  | Control room: serving CT room No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors - radiation protection: 2 x personnel access (900mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Essential Radiation proof glazing to control room Roller blind on cath. lab. room side Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0604
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0604 |  |  |  |  | Control room: serving CT room No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CLO005 |  | CLOCK impulse, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG074 |  | ILLUMINATED SIGN "DO NOT ENTER" | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT207 |  | SOCKET outlet aerial television, closed circuit (CCTV) | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE061 |  | SHELF, book, wall mounted with ends, 600W 200D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC016 |  | CABINET, base, modular storage, for 400 facing inserts, 4 drawers, on plinth, 900H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC017 |  | CABINET, base, modular storage, for 400 facing inserts, 3 drawers, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW054 |  | WORKTOP, clinical, for 4 x 400 facing modular storage cabinets, 1820W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB025 |  | CABINET, filing, 4 drawer, 1320H 465W 620D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA302 |  | CHAIR, swivel, height adjustable, medium back, wipeable, 5 star base, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0608
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0608 |  |  |  |  | Control room: serving 2 CT rooms No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Using the operating console to control each scan and monitor the VDT image. 2) Communicating with patient via two-way communication system. 3) X-ray films may be viewed. 4) Retrieving stored data. 5) Producing hard copy of selected CT images. 6) Communication with colleagues/offices/departments may occur by telephone. 7) Reference books and notices are studied. 8) Small items of equipment and sundries are stored. 9) Stationery/paper is stored. 10) Writing notes.
| Personnel: | [6 empty] | 6 x Staff With intermittent visitors.
| Planning Relationships: | [5 empty] | Adjacent to C.T. scanner room with visual/aural contact & direct access. Convenient to C.T. reporting room. Direct access to C.T. suite corridor.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 24 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | CT = Computed Tomography CT Operating console, data storage and hard copy unit - project team option. Good visual & voice contact with the CT scanner room. Activity note: Receiving colleagues/visitors for training/observation of C.T. session. Additional equipment notes: Direct wireway to CT scanner and diagnostic console positions. Link to departmental computer management system. Radiation protection as required. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0608
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0608 |  |  |  |  | Control room: serving 2 CT rooms No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Minimal fresh air requirement, cooling may be required, system design dictated by equipment requirements.
LIGHTING
| Type Of Control: | [13 empty] | V
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0608
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0608 |  |  |  |  | Control room: serving 2 CT rooms No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 3 sets of doors - radiation protection: 3 x personnel access (900mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Essential Radiation proof glazing to control room Roller blind on cath. lab. room side Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0608
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0608 |  |  |  |  | Control room: serving 2 CT rooms No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CLO005 |  | CLOCK impulse, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG074 |  | ILLUMINATED SIGN "DO NOT ENTER" | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT207 |  | SOCKET outlet aerial television, closed circuit (CCTV) | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE061 |  | SHELF, book, wall mounted with ends, 600W 200D | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SMC016 |  | CABINET, base, modular storage, for 400 facing inserts, 4 drawers, on plinth, 900H | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SMC017 |  | CABINET, base, modular storage, for 400 facing inserts, 3 drawers, on plinth, 900H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMW054 |  | WORKTOP, clinical, for 4 x 400 facing modular storage cabinets, 1820W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CAB025 |  | CABINET, filing, 4 drawer, 1320H 465W 620D | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | CHA302 |  | CHAIR, swivel, height adjustable, medium back, wipeable, 5 star base, on castors | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0701
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0701 |  |  |  |  | Waiting 'hot' room: post-injection, 5 patients Radionuclide
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may be ambulant, in a wheelchair or on a trolley or bed 2) Patient to wait post radio isotope administration for fairly long period. 3) Displaying and reading notices. 4) Viewing television.
| Personnel: | [6 empty] | 5 x Patients, including 1 trolley and 1 wheelchair patient.
| Planning Relationships: | [5 empty] | Adjacent to Injection Room & Gamma Camera Room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 20 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Space between the seats of approximately 0.80 metre, when measured centre to centre. The seating should have non-absorbent, wipe clean, finishes. Domestic environment desirable.
| ADB | [7 empty] | Room Environmental Data
E0701
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0701 |  |  |  |  | Waiting 'hot' room: post-injection, 5 patients Radionuclide
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V
| Daytime General Service Illuminance (Lux): | [13 empty] | 200 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0701
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0701 |  |  |  |  | Waiting 'hot' room: post-injection, 5 patients Radionuclide
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 1 x personnel, bed, trolley, wheelchair & equipment access (1500mm); 1 x approx 2200 mm Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0701
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0701 |  |  |  |  | Waiting 'hot' room: post-injection, 5 patients Radionuclide
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT206 |  | SOCKET outlet television aerial, single. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRA130 |  | TRACK, curtain, two sided, L-shape, 2400L 1800W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BRA015 |  | BRACKET, flat panel monitor, height adjustable, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | TVM003 |  | TELEVISION monitor, colour, flat panel, large, wall mounted | [16 empty] | 2
| 3 |  |  | 3 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0702
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0702 |  |  |  |  | Waiting 'hot' room: post-injection, 7 patients Radionuclide
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may be ambulant, in a wheelchair or on a trolley or bed 2) Patient to wait post radio isotope administration for fairly long period. 3) Displaying and reading notices. 4) Viewing television.
| Personnel: | [6 empty] | 7 x Patients, including 1 trolley and 1 wheelchair patient.
| Planning Relationships: | [5 empty] | Adjacent to Injection Room & Gamma Camera Room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 25 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Space between the seats of approximately 0.80 metre, when measured centre to centre. The seating should have non-absorbent, wipe clean, finishes. Domestic environment desirable.
| ADB | [7 empty] | Room Environmental Data
E0702
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0702 |  |  |  |  | Waiting 'hot' room: post-injection, 7 patients Radionuclide
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V
| Daytime General Service Illuminance (Lux): | [13 empty] | 200 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0702
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0702 |  |  |  |  | Waiting 'hot' room: post-injection, 7 patients Radionuclide
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 1 x personnel, bed, trolley, wheelchair & equipment access (1500mm); 1 x approx 2200 mm Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0702
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0702 |  |  |  |  | Waiting 'hot' room: post-injection, 7 patients Radionuclide
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL021 |  | LAMP repeat staff emergency call, ceiling mounted, (green) | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT206 |  | SOCKET outlet television aerial, single. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BRA015 |  | BRACKET, flat panel monitor, height adjustable, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLO001 |  | CLOCK battery, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | TVM003 |  | TELEVISION monitor, colour, flat panel, large, wall mounted | [16 empty] | 2
| 5 |  |  | 5 |  |  |  |  | CHA083 |  | CHAIR, stacking, polypropylene, with back and seat pads | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SCR011 |  | SCREEN, dividing, woodgrain melamine w PVC edge, freestanding, 1800H 1800W | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0709
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0709 |  |  |  |  | Holding Isotope room Radionuclide No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Holding of radio-isotopes. 2) Provision of refrigerated storage. 3) Storing syringe protectors and other similar equipment. 4) Miscellaneous equipment is stored. 5) Surgical instruments on instrument trolley may be used. 6) Clinical hand washing. 7) Disposal of radioactive liquid materials. 8) Holding contaminated used materials.
| Personnel: | [6 empty] | 1 - 2 Staff Intermittent use
| Planning Relationships: | [5 empty] | Adjacent to Injection room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Wash basin outlets connected directly to sewer. Sterility testing - Cabinet laminar flow (CAB123) is a project option or used in adjacent Pharmacy Department. 3x Boxes lead lined & 1x set of Bricks lead are project specific. Wall mounted telephone handset is required. "Controlled Area" warning sign. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0709
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0709 |  |  |  |  | Holding Isotope room Radionuclide No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0709
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0709 |  |  |  |  | Holding Isotope room Radionuclide No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - radiation protection: 1 x personnel, trolley & equipment access (1500mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0709
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0709 |  |  |  |  | Holding Isotope room Radionuclide No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC011 |  | CABINET, base, modular storage, for 400 facing inserts, open, on plinth, 900H | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | SMC021 |  | CABINET, upper, modular storage, for 400 facing inserts, open, 750H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMW081 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 2100W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN025 |  | BIN, disposal, standard, pedal, epoxy coated steel, radioisotope symbol, 17 litres 6mm lead, 640H 240W 360D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | REF025 |  | REFRIGERATOR, capacity 112 litres, 3mm lead lined, isotope symbol | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SAF002 |  | SAFE, radioisotopes, lead lined, 600H 450W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT001 |  | TROLLEY, modular storage, single open frame, including handle, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0710
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0710 |  |  |  |  | Injection, isotope holding room Radionuclide No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Holding of radio-isotopes. 2) Provision of refrigerated storage. 3) Patients' trolley(s) may be parked or stored. 4) Administration of radio isotope injection. 5) Storing syringe protectors and other similar equipment. 6) Miscellaneous equipment is stored. 7) Surgical instruments on instrument trolley may be used. 8) Disposal of radioactive liquid materials. 9) Holding contaminated used materials. 10) Resuscitation trolley and associated equipment may be used. 11) Clinical hand washing.
| Personnel: | [6 empty] | 1 x Patient 2 x Staff Intermittent use
| Planning Relationships: | [5 empty] | Adjacent to "Hot" waiting room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 18 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Wash basin outlets connected directly to sewer for radiation protection. Sterility testing - Cabinet laminar flow (CAB123) is a project option or used in adjacent Pharmacy Department. 3x Boxes lead lined & 1x set of Bricks lead are project specific. A patient weighing machine may be required. Wall mounted telephone handset is required. "Controlled Area" warning sign. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0710
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0710 |  |  |  |  | Injection, isotope holding room Radionuclide No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0710
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0710 |  |  |  |  | Injection, isotope holding room Radionuclide No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - radiation protection: 1 x personnel, trolley & equipment access (1500mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0710
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0710 |  |  |  |  | Injection, isotope holding room Radionuclide No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC011 |  | CABINET, base, modular storage, for 400 facing inserts, open, on plinth, 900H | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SMC021 |  | CABINET, upper, modular storage, for 400 facing inserts, open, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW081 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 2100W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAB123 |  | *CABINET, vertical laminar flow, safety model, floor standing, 2375H 1800W 980D. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN025 |  | BIN, disposal, standard, pedal, epoxy coated steel, radioisotope symbol, 17 litres 6mm lead, 640H 240W 360D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF025 |  | REFRIGERATOR, capacity 112 litres, 3mm lead lined, isotope symbol | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT001 |  | TROLLEY, modular storage, single open frame, including handle, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SUC005 |  | SUCTION UNIT, electric, mobile, 845H 470W 410D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO070 |  | TROLLEY, for single cylinder, type F or G, 1155H 510W 405D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | VEN038 |  | VENTILATOR radioaerosol delivery system, inspiration only, 375H 200W 150D, comprising: Nebuliser, Sizer, Air supply tubing, External loader, Reservoir bag, Valves, Mouthpiece, Filter traps, Lead shield box | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0711
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0711 |  |  |  |  | Injection room Radionuclide No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patients' trolley(s) may be parked or stored. 2) Administration of radio isotope injection. 3) Surgical instruments on instrument trolley may be used. 4) Resuscitation trolley and associated equipment may be used. 5) Clinical hand washing.
| Personnel: | [6 empty] | 1 x Patient 2 x Staff Intermittent use
| Planning Relationships: | [5 empty] | Adjacent to "Hot" waiting room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Wash basin outlets connected directly to sewer for radiation protection. A patient weighing machine may be required. Wall mounted telephone handset is required. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0711
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0711 |  |  |  |  | Injection room Radionuclide No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | +Ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0711
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0711 |  |  |  |  | Injection room Radionuclide No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - radiation protection: 1 x personnel, trolley, wheelchair & equipment access (1500mm) Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0711
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0711 |  |  |  |  | Injection room Radionuclide No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL003 |  | PUSH BUTTON, patient/staff call (help) with socket for patient hand-held unit | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL029 |  | LAMP patient reassurance, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN025 |  | BIN, disposal, standard, pedal, epoxy coated steel, radioisotope symbol, 17 litres 6mm lead, 640H 240W 360D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA356 |  | CHAIR, venepuncture, wipeable. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COU007 |  | COUCH, examination/treatment, (2 section), with paper roll holder, variable height, retractable wheels | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SCA081 |  | SCALE COLUMN, weighing person, with sliding weights, and telescopic column for height measure | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT001 |  | TROLLEY, modular storage, single open frame, including handle, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SUC005 |  | SUCTION UNIT, electric, mobile, 845H 470W 410D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO070 |  | TROLLEY, for single cylinder, type F or G, 1155H 510W 405D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | VEN038 |  | VENTILATOR radioaerosol delivery system, inspiration only, 375H 200W 150D, comprising: Nebuliser, Sizer, Air supply tubing, External loader, Reservoir bag, Valves, Mouthpiece, Filter traps, Lead shield box | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0713
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0713 |  |  |  |  | Imaging room: Gamma Camera multi detector with stress facility Radionuclide
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may be ambulant, in a wheelchair or on a trolley or bed 2) Positioning patient on examination couch stress inducing equipment or chair. 3) Radionuclide imaging examination of patient. 4) Use of Multiformat Imager or other hard copy device. 5) Patient to undergo exercise stress/rest test. 6) Clinical hand washing. 7) Small items of equipment and sundries are stored. 8) Data disks (CDs/DVDs) are stored. 9) Holding/ storing personal belongings. 10) Displaying notices.
| Personnel: | [6 empty] | Patient and 2-3 staff (including Escort where needed).
| Planning Relationships: | [5 empty] | txtPlanningRelationships
| Space Data: | [6 empty] | Area (m²): |  |  |  | 36 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | txtRoomNotes
| ADB | [7 empty] | Room Environmental Data
E0713
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0713 |  |  |  |  | Imaging room: Gamma Camera multi detector with stress facility Radionuclide
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6 |  | No intrusive procedures
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V/Sp
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 100 |  | On couch
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Non-ionising for rooms with x-ray machines
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0713
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0713 |  |  |  |  | Imaging room: Gamma Camera multi detector with stress facility Radionuclide
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - radiation protection: 1 x personnel, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0713
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0713 |  |  |  |  | Imaging room: Gamma Camera multi detector with stress facility Radionuclide
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC091 |  | CABINET base, 400mm facing, (400x600 inserts), with formed plastic liners, 1 door hinged right, on plinth, o/a height 900 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC092 |  | CABINET base, 400mm facing, (400x600 inserts), with formed plastic liners, 1 door hinged left, on plinth, o/a height 900 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC096 |  | CABINET base, 400mm facing, (400x600 inserts), with 3 telescopic runners, 1 door hinged left, on plinth, o/a height 900 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC127 |  | CABINET top, 600mm facing, (600x400 inserts), with formed plastic liners, 1 door hinged right, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSW013 |  | WORKTOP, for 3x 400mm facing inserts cabinets, 1365W 700D nominal | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT059 |  | CONNECTION UNIT switched 13amp, flex, indicator light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLO004 |  | CLOCK battery with second sweep hand, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | ILL010 |  | ILLUMINATOR, x-ray film, double, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG071 |  | IMAGER GAMMA CAMERA, digital, multi detector, with monitor | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG073 |  | TABLE PATIENT - SPECT, gamma camera, variable height, 970/730H 2060W 720D, Part of gamma camera) | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0713
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0713 |  |  |  |  | Imaging room: Gamma Camera multi detector with stress facility Radionuclide
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | IMG074 |  | IMAGER COLLIMATOR RACK, gamma camera, 1300H 770W 800D, (Included in IMG070, IMG071, IMG091) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG076 |  | IMAGER CART exchange collimator, gamma camera, 1270H 670W 910D, (Part of IMG070 and IMG072) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG077 |  | CONSOLE UNIT and COMPUTER for gamma camera/PET, 1180H 1040W 900D, (Included in IMG070, IMG071, IMG072 and IMG091) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG079 |  | IMAGER DISK UNIT optical, (Part of IMG077) | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | LOC012 |  | LOCKER, wall mounted, 340H 300W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN025 |  | BIN, disposal, standard, pedal, epoxy coated steel, radioisotope symbol, 17 litres 6mm lead, 640H 240W 360D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA017 |  | CHAIR, upright, upholstered, stacking | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | EXE014 |  | EXERCISE BICYCLE, ergometer | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG109 |  | IMAGING CHAIR, with arms, tilt, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SCR064 |  | SCREEN, x-ray radiation protection, lead rubber, mobile, 900H 700L, lead equivalent 0.5mm Pb. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0714
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0714 |  |  |  |  | Imaging room: Gamma Camera multi detector SPECT Radionuclide
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may be ambulant, in a wheelchair or on a trolley or bed 2) Patient is positioned or repositioned on examination/treatment couch or in a chair. 3) Radionuclide imaging examination of patient. 4) Use of Multiformat Imager or other hard copy device. 5) Clinical hand washing. 6) Small items of equipment and sundries are stored. 7) Data disks (CDs/DVDs) are stored. 8) Holding/ storing personal belongings. 9) Displaying notices.
| Personnel: | [6 empty] | Patient and 2-3 staff (including Escort where needed).
| Planning Relationships: | [5 empty] | Adjacent to "Hot" waiting room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 36 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | SPECT = Single photon emission computed tomography. Lamp indicator call situated over door outside room. Radiation protection mobile screen or fixed shielding is required. Drain must go direct to sewer for radiation protection purposes. "Supervised Area" warning sign. Gamma Camera PET and computer need clean electrical supply and with the A/C system need be on essential. Link to departmental computer management system/PACS.
| ADB | [7 empty] | Room Environmental Data
E0714
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0714 |  |  |  |  | Imaging room: Gamma Camera multi detector SPECT Radionuclide
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6 |  | No intrusive procedures
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V/Sp
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 100 |  | On couch
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Non-ionising for rooms with x-ray machines
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0714
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0714 |  |  |  |  | Imaging room: Gamma Camera multi detector SPECT Radionuclide
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - radiation protection: 1 x personnel, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0714
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0714 |  |  |  |  | Imaging room: Gamma Camera multi detector SPECT Radionuclide
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC091 |  | CABINET base, 400mm facing, (400x600 inserts), with formed plastic liners, 1 door hinged right, on plinth, o/a height 900 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC092 |  | CABINET base, 400mm facing, (400x600 inserts), with formed plastic liners, 1 door hinged left, on plinth, o/a height 900 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC096 |  | CABINET base, 400mm facing, (400x600 inserts), with 3 telescopic runners, 1 door hinged left, on plinth, o/a height 900 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC127 |  | CABINET top, 600mm facing, (600x400 inserts), with formed plastic liners, 1 door hinged right, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSW013 |  | WORKTOP, for 3x 400mm facing inserts cabinets, 1365W 700D nominal | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT059 |  | CONNECTION UNIT switched 13amp, flex, indicator light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLO004 |  | CLOCK battery with second sweep hand, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | ILL010 |  | ILLUMINATOR, x-ray film, double, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG072 |  | IMAGER GAMMA CAMERA, digital, multi detector/PET, with monitor | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG073 |  | TABLE PATIENT - SPECT, gamma camera, variable height, 970/730H 2060W 720D, Part of gamma camera) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG075 |  | IMAGER COLLIMATOR RACK, gamma camera PET, (Included in IMG072 and IMG091) | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0714
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0714 |  |  |  |  | Imaging room: Gamma Camera multi detector SPECT Radionuclide
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | IMG076 |  | IMAGER CART exchange collimator, gamma camera, 1270H 670W 910D, (Part of IMG070 and IMG072) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG077 |  | CONSOLE UNIT and COMPUTER for gamma camera/PET, 1180H 1040W 900D, (Included in IMG070, IMG071, IMG072 and IMG091) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG079 |  | IMAGER DISK UNIT optical, (Part of IMG077) | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | LOC012 |  | LOCKER, wall mounted, 340H 300W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN025 |  | BIN, disposal, standard, pedal, epoxy coated steel, radioisotope symbol, 17 litres 6mm lead, 640H 240W 360D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA017 |  | CHAIR, upright, upholstered, stacking | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | IMG109 |  | IMAGING CHAIR, with arms, tilt, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SCR064 |  | SCREEN, x-ray radiation protection, lead rubber, mobile, 900H 700L, lead equivalent 0.5mm Pb. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0801
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0801 |  |  |  |  | Scanner room: Magnetic Resonance Imaging (MRI) closed bore No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient to arrive on foot or on MRI trolley, having been prepared for examination. 2) Positioning/repositioning patient on the scanner table/couch. 3) Patient undergoes scanning with constant aural/visual contact and possible vital function monitoring. 4) Interventional work or imaging procedure examination. 5) Administration of intravenous analgesia. 6) Maintenance of sedation during examination using appropriate equipment. 7) Patient to be removed from scanner in emergency and taken out of scanner room for emergency procedures/resuscitation. 8) Holding MR coils. 9) Storing MRI compatible equipment. 10) Small items of equipment are held stored 11) Disposable items are stored.
| Personnel: | [6 empty] | 1 x Patient 2 - 8 Staff Intermittent use
| Planning Relationships: | [5 empty] | Convenient to Reporting Room with visual contact. Adjacent to Control Room. Close to sub-waiting. Close to recovery bay. Close to resuscitation. Adjacent to technical equipment room incl. gradient amplifiers, RF generators. Convenient to service entrance for cryogens delivery. Position on external wall assist venting requirement & changing of magnet (via removable panel/section).
| Space Data: | [6 empty] | Area (m²): |  |  |  | 45 |  |  |  |  | Height (mm): |  |  |  | 3000
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Space required for the equipment MRI compatible which may be stored elsewhere: Anaesthetic machine (ANA007), Infusion pump (STA145). Equipment to be non-ferromagnetic and use authorised materials, e.g.: brass coat hooks, notice boards, chairs - non metallic. Room to have total radio-frequency (RF) radiation screening. Provision of facility such as taped music, relaxation murals should be considered. All electrical circuits into room must be fitted with line RF filters. Wireways & pipe routes to technical equipment & control room to be via RF shielded access ports (waveguides). An "emergency stop" button which cuts power to the computer console & stop the examination.
| ADB | [7 empty] | Room Environmental Data
E0801
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0801 |  |  |  |  | Scanner room: Magnetic Resonance Imaging (MRI) closed bore No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Non condensing
| General Notes: | [5 empty] | Fresh air for two people. Emergency extract in event of low oxygen being detected. Temperature, humidity and rate of change in temperature to be kept within limits stated by manufacturer to prevent condensation and thermal shock inside equipment.
LIGHTING
| Type Of Control: | [13 empty] | V/Sp
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | On working plane. Electronic, electrical equipment should be constructed with no ferrous/copper metallic parts where possible or located outside of the magnetic field generated by the MRI scanner
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 100 |  | On couch
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Aspiration with non ferrite pipework to MRI rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0801
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0801 |  |  |  |  | Scanner room: Magnetic Resonance Imaging (MRI) closed bore No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - RF shielded: 1 x personnel, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Essential Radiation proof glazing to control room Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0801
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0801 |  |  |  |  | Scanner room: Magnetic Resonance Imaging (MRI) closed bore No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP112 |  | CUPBOARD UNIT, non-ferrous, open, 3 adjustable shelf, on plinth, 850H 1000W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP116 |  | CUPBOARD/DRAWER UNIT, non-ferrous, 2 drawer, 1 adjustable shelf, on plinth, 850H 1000W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | IMG081 |  | IMAGER, MAGNETIC RESONANCE IMAGING (MRI), closed bore. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | IMG086 |  | TABLE PATIENT - MRI imager, floating top, (Part of IMG081) | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG052 |  | LUMINAIRE operating (minor), low ferrous metal content | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT461 |  | OUTLET, nitrous oxide, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SUC002 |  | SUCTION UNIT, pipeline, high pressure, theatre | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC001 |  | SWITCH 5amp ac single pole, 1 way, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC062 |  | EMERGENCY STOP switch button, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WOR130 |  | WORKTOP, 2500W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CHA023 |  | CHAIR, upright, wood | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MON051 |  | MONITOR, patient, MR compatible, vital signs, multi-parameter, includes pulse oximeter, 280H 360W 215D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SYR005 |  | SYRINGE INJECTOR, MRI compatible, automatic, hi pressure injection, media contrast | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO139 |  | TROLLEY, dressing/instrument, MRI compatible, 870H 450W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0802
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0802 |  |  |  |  | Technical equipment room: serving MRI close bore
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Housing RF generating equipment and gradient amplifiers. 2) Housing auxiliary conservation plant for cryogen system.
| Personnel: | [6 empty] | 1 x Person Intermittent use
| Planning Relationships: | [5 empty] | Adjacent to scanner room. Good access for plant & equipment.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 20 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Equipment to be project specific.
| ADB | [7 empty] | Room Environmental Data
E0802
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0802 |  |  |  |  | Technical equipment room: serving MRI close bore
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 20
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 0.5
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Minimal fresh air requirement, system design dictated by equipment requirements.
LIGHTING
| Type Of Control: | [13 empty] | V/Sp
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | on working plane
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0802
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0802 |  |  |  |  | Technical equipment room: serving MRI close bore
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0802
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0802 |  |  |  |  | Technical equipment room: serving MRI close bore
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0804
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0804 |  |  |  |  | Control room: serving MRI
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Using the operating console to control each scan and monitor the VDT image. 2) Communicating with patient via two-way communication system. 3) X-ray films may be viewed. 4) Retrieving and archiving stored data. 5) Producing hard copy of selected MR images. 6) Initiate the processing of films using dry laser printer to produce hard copies. 7) Communication with colleagues/offices/departments may occur by telephone. 8) Controlling access to MRI Scanner room. 9) Reference books and notices are studied. 10) Small items of equipment and sundries are stored. 11) Stationery/paper is stored. 12) Writing notes.
| Personnel: | [6 empty] | 3 x Staff (radiographers & a radiologist) Other persons may include radiographers, clinicians incl. surgeons & anesthetists. With intermittent visitors.
| Planning Relationships: | [5 empty] | Adjacent to MRI scanner room with visual/aural contact. Adjacent to MRI office & reporting. Direct access to MRI suite corridor.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 16 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | MRI Operating console, data storage and hard copy unit - project team option. Receiving colleagues/visitors for training/observation of MRI session. Wireways to MRI scanner to be via RF- shielded access ports (inc. spare capacity for future use). Direct wireway between diagnostic console position and departmental laser imaging equipment. Variable lighting control. Link to departmental computer management system/PACS. Local temperature control required. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0804
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0804 |  |  |  |  | Control room: serving MRI
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Minimal fresh air requirement, system design dictated by equipment requirements.
LIGHTING
| Type Of Control: | [13 empty] | V/Sp
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | on working plane
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 100 |  | On couch
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0804
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0804 |  |  |  |  | Control room: serving MRI
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Essential Radiation proof glazing to control room Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0804
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0804 |  |  |  |  | Control room: serving MRI
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CLO005 |  | CLOCK impulse, wall mounted | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT207 |  | SOCKET outlet aerial television, closed circuit (CCTV) | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE231 |  | SHELF, 1500W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | WOR073 |  | WORKTOP, 1500W 900D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 6 |  |  | 6 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STF130 |  | STORAGE UNIT, lower, cupboard, 2 door, 1 shelf, on castors, 600H 600W 550D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STF165 |  | STORAGE UNIT, lower, 6 drawer, on castors, 600H 600W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0811
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0811 |  |  |  |  | Control room: serving 2 MRI rooms No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Using the operating console to control each scan and monitor the VDT image. 2) Communicating with patient via two-way communication system. 3) X-ray films may be viewed. 4) Retrieving stored data. 5) Producing hard copy of selected MR images. 6) Communication with colleagues/offices/departments may occur by telephone. 7) Controlling access to MRI Scanner room. 8) Reference books and notices are studied. 9) Small items of equipment and sundries are stored. 10) Stationery/paper is stored. 11) Writing notes.
| Personnel: | [6 empty] | 6 x Staff (radiographers & a radiologist) Other persons may include radiographers, clinicians incl. surgeons & anesthetists. With intermittent visitors.
| Planning Relationships: | [5 empty] | Adjacent to MRI scanner room with visual/aural contact. Adjacent to MRI office & reporting. Direct access to MRI suite corridor.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 24 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | MRI Operating console, data storage and hard copy unit - project team option. Receiving colleagues/visitors for training/observation of MRI session. Wireways to MRI scanner to be via RF- shielded access ports (inc. spare capacity for future use). Direct wireway between diagnostic console position and departmental laser imaging equipment. Variable lighting control. Link to departmental computer management system. Local temperature control required. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0811
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0811 |  |  |  |  | Control room: serving 2 MRI rooms No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Minimal fresh air requirement, system design dictated by equipment requirements.
LIGHTING
| Type Of Control: | [13 empty] | V/Sp
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 100 |  | On couch
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0811
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0811 |  |  |  |  | Control room: serving 2 MRI rooms No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 doorset: 2 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Essential Radiation proof glazing to control room Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0811
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0811 |  |  |  |  | Control room: serving 2 MRI rooms No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 3 |  |  | 3 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT207 |  | SOCKET outlet aerial television, closed circuit (CCTV) | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE231 |  | SHELF, 1500W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | WOR073 |  | WORKTOP, 1500W 900D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 7 |  |  | 7 |  |  |  |  | CHA302 |  | CHAIR, swivel, height adjustable, medium back, wipeable, 5 star base, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STF130 |  | STORAGE UNIT, lower, cupboard, 2 door, 1 shelf, on castors, 600H 600W 550D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STF165 |  | STORAGE UNIT, lower, 6 drawer, on castors, 600H 600W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0901
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0901 |  |  |  |  | Scanner room: Positron Emission Tomography (PET)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient will arrive on trolley. 2) Positioning/repositioning patient on the scanner table/couch. 3) Radionuclide imaging examination of patient using PET scanner. 4) Radiation protection equipment will be used. 5) Patient undergoes scanning with constant aural/visual contact and possible vital function monitoring. 6) Clinical hand washing. 7) Small items of equipment and sundries are stored. 8) Holding/ storing personal belongings. 9) Displaying notices.
| Personnel: | [6 empty] | 1 x Patient 2 -3 Staff
| Planning Relationships: | [5 empty] | Adjacent to "Hot" waiting room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 27 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Provision of facility such as taped music should be considered. Clinical WHB labelled & designated not for the disposal of radioactive waste. Radiation protection mobile screen or fixed shielding is be required. Cupboards under worktop shielded with appropriate thickness of lead sheet, to be suitable for storage radioactive calibration equipment used to perform attenuation correction on the PET scanner. PET scanner need clean electrical supply and with the A/C system need be on essential. "Supervised Area" warning sign. Link to departmental computer management system. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0901
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0901 |  |  |  |  | Scanner room: Positron Emission Tomography (PET)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Minimal fresh air requirement, system design dictated by equipment requirements.
LIGHTING
| Type Of Control: | [13 empty] | V/Sp
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 100 |  | On couch
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Non-ionising for rooms with x-ray machines
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0901
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0901 |  |  |  |  | Scanner room: Positron Emission Tomography (PET)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - radiation protection: 1 x personnel, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
For the constructional radiation protection requirements refer to text guidance - Maze may be required. All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0901
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0901 |  |  |  |  | Scanner room: Positron Emission Tomography (PET)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT207 |  | SOCKET outlet aerial television, closed circuit (CCTV) | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SHE241 |  | SHELF, 1800W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC011 |  | CABINET, base, modular storage, for 400 facing inserts, open, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC016 |  | CABINET, base, modular storage, for 400 facing inserts, 4 drawers, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC073 |  | CABINET, upper, modular storage, for 600 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW054 |  | WORKTOP, clinical, for 4 x 400 facing modular storage cabinets, 1820W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG073 |  | TABLE PATIENT - SPECT, gamma camera, variable height, 970/730H 2060W 720D, Part of gamma camera) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG074 |  | IMAGER COLLIMATOR RACK, gamma camera, 1300H 770W 800D, (Included in IMG070, IMG071, IMG091) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG076 |  | IMAGER CART exchange collimator, gamma camera, 1270H 670W 910D, (Part of IMG070 and IMG072) | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0901
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0901 |  |  |  |  | Scanner room: Positron Emission Tomography (PET)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | IMG077 |  | CONSOLE UNIT and COMPUTER for gamma camera/PET, 1180H 1040W 900D, (Included in IMG070, IMG071, IMG072 and IMG091) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG091 |  | IMAGER SCANNER POSITRON EMISSION TOMOGRAPHY (PET) | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | LOC012 |  | LOCKER, wall mounted, 340H 300W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN025 |  | BIN, disposal, standard, pedal, epoxy coated steel, radioisotope symbol, 17 litres 6mm lead, 640H 240W 360D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA302 |  | CHAIR, swivel, height adjustable, medium back, wipeable, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC197 |  | RACK, x-ray lead apron, 6 swivel arms, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO135 |  | TROLLEY, dressing/equipment, 6 clear trays, buffered, 890H 510W 480D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0902
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0902 |  |  |  |  | Control room: serving PET No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Using the operating console to control each scan and monitor the VDT image. 2) Communicating with patient via two-way communication system. 3) Viewing, retrieving and archiving x-ray films/images. 4) Producing hard copy of selected PET images. 5) Communication with colleagues/offices/departments may occur by telephone. 6) Small items of equipment and sundries are stored. 7) Stationery/paper is stored. 8) Writing notes.
| Personnel: | [6 empty] | 3 x Staff (2 Radiographers, 1 Radiologist)
| Planning Relationships: | [5 empty] | Adjacent to PET scanner room. Direct access to a corridor or other shared areas.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 16 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | PET Operating console, data storage and hard copy unit - project team option. Direct wireway between diagnostic console position and departmental laser imaging equipment. Variable lighting control. Link to departmental computer management system/PACS. Local temperature control required. Radiation protection advice required. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0902
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0902 |  |  |  |  | Control room: serving PET No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Minimal fresh air requirement, system design dictated by equipment requirements.
LIGHTING
| Type Of Control: | [13 empty] | V/Sp
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | at 1m AFFL. 2 Way switching of lights at door and by control desk (control desk may be in a separate room)
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 100 |  | On couch
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0902
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0902 |  |  |  |  | Control room: serving PET No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Essential Radiation proof glazing to control room Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0902
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0902 |  |  |  |  | Control room: serving PET No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT207 |  | SOCKET outlet aerial television, closed circuit (CCTV) | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE231 |  | SHELF, 1500W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC016 |  | CABINET, base, modular storage, for 400 facing inserts, 4 drawers, on plinth, 900H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC017 |  | CABINET, base, modular storage, for 400 facing inserts, 3 drawers, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW054 |  | WORKTOP, clinical, for 4 x 400 facing modular storage cabinets, 1820W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | IMG077 |  | CONSOLE UNIT and COMPUTER for gamma camera/PET, 1180H 1040W 900D, (Included in IMG070, IMG071, IMG072 and IMG091) | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CHA302 |  | CHAIR, swivel, height adjustable, medium back, wipeable, 5 star base, on castors | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0904
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0904 |  |  |  |  | Radiopharmaceutical delivery, preparation, disposal hold PET No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Preparing radiopharmaceutical products by open procedures under laminar flow within a workstation using aseptic techniques. 2) Holding of radio-isotopes. 3) Storing drugs/medicines. 4) Storing equipment for use in preparing radiopharmaceuticals. 5) Disposal of radioactive liquid materials. 6) Holding contaminated used materials.
| Personnel: | [6 empty] | 2 x Staff
| Planning Relationships: | [5 empty] | Adjacent to Scanner room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | 3x Boxes lead lined and 1x set of Bricks lead are project specific. In preparation area, a section of worktop should be shielded in lead/plywood laminate lead equivalent thickness 1cm. Wall mounted telephone handset is required. "Controlled Area" warning sign. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
E0904
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0904 |  |  |  |  | Radiopharmaceutical delivery, preparation, disposal hold PET No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | +ve if preparation,<BR>-ve if disposal hold
| Supply Air: Final Filter Class | [12 empty] | F7/>H10
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Level of cleanliness required not clear from room description.
LIGHTING
| Type Of Control: | [13 empty] | V/Sp
| Daytime General Service Illuminance (Lux): | [13 empty] | 500 |  | On working plane. Dimmable lighting
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0904
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0904 |  |  |  |  | Radiopharmaceutical delivery, preparation, disposal hold PET No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - radiation protection: 1 x personnel, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0904
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0904 |  |  |  |  | Radiopharmaceutical delivery, preparation, disposal hold PET No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC011 |  | CABINET, base, modular storage, for 400 facing inserts, open, on plinth, 900H | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC021 |  | CABINET, upper, modular storage, for 400 facing inserts, open, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW081 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 2100W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAB123 |  | *CABINET, vertical laminar flow, safety model, floor standing, 2375H 1800W 980D. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN025 |  | BIN, disposal, standard, pedal, epoxy coated steel, radioisotope symbol, 17 litres 6mm lead, 640H 240W 360D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SAF002 |  | SAFE, radioisotopes, lead lined, 600H 450W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SCR064 |  | SCREEN, x-ray radiation protection, lead rubber, mobile, 900H 700L, lead equivalent 0.5mm Pb. | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | E0905
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0905 |  |  |  |  | Waiting room: injection and post-injection wait PET No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Weighing and measuring height of a patient. 2) Administration of radio isotope injection. 3) Patient to wait post radio isotope administration for fairly long period. 4) Clinical hand washing. 5) Storing syringe protectors and other similar equipment. 6) Storing/using radioactive isotopes.
| Personnel: | [6 empty] | 1 x Patient 1 - 2 Staff
| Planning Relationships: | [5 empty] | Direct access from Preparation area. Adjacent to Scanner room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 9 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Following injection, the patient typically lies still for an hour or more, to limit muscular uptake of FDG (FluoroDeoxyGlucose) prior to scanning. Wash basin outlets connected directly to sewer. Radiation protect advice is essential for this room and adjacent areas due to high levels of radioactivity over a long period. (Solid concrete walls may be necessary.)
| ADB | [7 empty] | Room Environmental Data
E0905
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0905 |  |  |  |  | Waiting room: injection and post-injection wait PET No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | +Ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | V/Sp
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | on bed/couch level. Dimmable lighting.
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | E0905
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0905 |  |  |  |  | Waiting room: injection and post-injection wait PET No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | E0905
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | E0905 |  |  |  |  | Waiting room: injection and post-injection wait PET No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL003 |  | PUSH BUTTON, patient/staff call (help) with socket for patient hand-held unit | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL021 |  | LAMP repeat staff emergency call, ceiling mounted, (green) | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA391 |  | CHAIR, easy, reclining, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SCA081 |  | SCALE COLUMN, weighing person, with sliding weights, and telescopic column for height measure | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT001 |  | TROLLEY, modular storage, single open frame, including handle, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0171
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0171 |  |  |  |  | Parking bay: large equipment
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Parking equipment. 2) Equipment is placed on charge.
| Personnel: | [6 empty] | Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 4 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
G0171
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0171 |  |  |  |  | Parking bay: large equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | See HVAC notes 2
| Ventilation Type: | [13 empty] | N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
| General Notes: | [5 empty] | Part of corridor space
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0171
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0171 |  |  |  |  | Parking bay: large equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0171
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0171 |  |  |  |  | Parking bay: large equipment
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0180-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0180-01 |  |  |  |  | Parking bay: resusitation trolley
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Mobile equipment may be parked and stored and/or recharged. 2) Equipment is placed on charge. 3) Carrying out routine checks on equipment.
| Personnel: | [6 empty] | Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
G0180-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0180-01 |  |  |  |  | Parking bay: resusitation trolley
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | See HVAC notes 2
| Ventilation Type: | [13 empty] | N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
| General Notes: | [5 empty] | Part of corridor space
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0180-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0180-01 |  |  |  |  | Parking bay: resusitation trolley
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0180-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0180-01 |  |  |  |  | Parking bay: resusitation trolley
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRO310 |  | TROLLEY, emergency/resuscitation, complete with defibrillator, 955H 825W 575D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0180-06
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0180-06 |  |  |  |  | Parking bay: mobile x-ray unit
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Mobile equipment may be parked and stored and/or recharged. 2) Equipment is placed on charge.
| Personnel: | [6 empty] | Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
G0180-06
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0180-06 |  |  |  |  | Parking bay: mobile x-ray unit
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | See HVAC notes 2
| Ventilation Type: | [13 empty] | N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
| General Notes: | [5 empty] | Part of corridor space
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0180-06
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0180-06 |  |  |  |  | Parking bay: mobile x-ray unit
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0180-06
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0180-06 |  |  |  |  | Parking bay: mobile x-ray unit
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAC197 |  | RACK, x-ray lead apron, 6 swivel arms, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | XRA007 |  | X-RAY IMAGING UNIT, adjustable arm 1840/580mm, electric, mobile, battery driven, 1840H 2240W 660W | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0180-10
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0180-10 |  |  |  |  | Parking bay: 3 wheelchairs
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Mobile equipment may be parked and stored and/or recharged. 2) Equipment is placed on charge.
| Personnel: | [6 empty] | Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
G0180-10
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0180-10 |  |  |  |  | Parking bay: 3 wheelchairs
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | See HVAC notes 2
| Ventilation Type: | [13 empty] | N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
| General Notes: | [5 empty] | Part of corridor space
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0180-10
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0180-10 |  |  |  |  | Parking bay: 3 wheelchairs
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0180-10
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0180-10 |  |  |  |  | Parking bay: 3 wheelchairs
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0710
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0710 |  |  |  |  | Telephone booth
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Payphone may be used.
| Personnel: | [6 empty] | 1 x person.
| Planning Relationships: | [5 empty] | Within easy access.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 1.5 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | All public telephones should include a shelf to enable a person with a hearing impairment to use a portable text phone. The following items are shown on the room layout but are optional: - acoustic hood. - Where provided, it should be designed and mounted in such a way that it is not a hazard to disabled people i.e. by ensuring that it is located outside any circulation route or by provision of a hazard warning.
| ADB | [7 empty] | Room Environmental Data
G0710
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0710 |  |  |  |  | Telephone booth
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | n/a
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 100
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 300 |  | On telephone
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 43
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 43 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0710
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0710 |  |  |  |  | Telephone booth
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0710
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0710 |  |  |  |  | Telephone booth
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT220 |  | SOCKET, outlet telephone, part of TEL004 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TEL004 |  | TELEPHONE handset coin/card operated, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | TEL019 |  | TELEPHONE HOOD, acoustic, wall mounted | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0712
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0712 |  |  |  |  | Telephone booth: wheelchair accessible
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Payphone may be used.
| Personnel: | [6 empty] | 1 x person.
| Planning Relationships: | [5 empty] | Within easy access.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | Telephones for wheelchair users should be located to enable access from the front and side. This is assumed in the room layout. Where it is only possible to approach the telephone from the front, a knee hole at least 500 mm deep and 700 mm high should be provided This space includes a fold-down seat (450-520 mm high), alternatively, it can accommodate a perch seat (650-800 mm high) for ambulant users only.
| ADB | [7 empty] | Room Environmental Data
G0712
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0712 |  |  |  |  | Telephone booth: wheelchair accessible
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | n/a
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 100
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 300 |  | On telephone
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 44
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 44 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0712
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0712 |  |  |  |  | Telephone booth: wheelchair accessible
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0712
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | G0712 |  |  |  |  | Telephone booth: wheelchair accessible
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT220 |  | SOCKET, outlet telephone, part of TEL004 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | RAI046 |  | RAIL, grab, vertical, wall mounted, 450mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SEA024 |  | SEAT, tip-up, wall mounted, 400 W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TEL004 |  | TELEPHONE handset coin/card operated, wall mounted | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | H0335
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | H0335 |  |  |  |  | Study, quiet room: 5 patients
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may be ambulant or in a wheelchair. 2) Specialised visual aids and multi-media equipment may be used. 3) Computer workstation(s) may be used.
| Personnel: | [6 empty] | 5 x Persons 1 x Staff
| Planning Relationships: | [5 empty] | Close to Library Service Area. Quiet location.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 18 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Magnetic board can be replaced by Velcro board - project team option. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
H0335
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | H0335 |  |  |  |  | Study, quiet room: 5 patients
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or +ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 300 |  | Over desk task area
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 50 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | H0335
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | H0335 |  |  |  |  | Study, quiet room: 5 patients
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control. Window opening restrictors 100mm at bottom Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | H0335
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | H0335 |  |  |  |  | Study, quiet room: 5 patients
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA017 |  | BOARD, display/notice, magnetic, wall mounted, 1200H 1200W | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CAR001 |  | CARREL, single sided study, freestanding, strap light and socket outlet | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA378 |  | UNIT CHAIR, easy, with arms, fully upholstered, wipeable, | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA379 |  | UNIT CHAIR/SETTEE, 2 seater, easy, with arms, fully upholstered, wipeable. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SHE127 |  | SHELF BOOK UNIT, 5 shelves, single sided, open, freestanding, 2000H 800W 250D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | SHE128 |  | SHELF BOOK UNIT, 3 shelves, double sided, open, island, 1370H 900W 500D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB008 |  | TABLE, 710H 1200W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB011 |  | TABLE, 725H 1220W 750D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB056 |  | TABLE, occasional, round, 415H 610mm dia. | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | H1304-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | H1304-01 |  |  |  |  | Seminar room: 10 places (including 1 wheelchair place)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Seminars/conferences are held. 2) Multimedia equipment may be used. 3) Laptop computer(s) may be used. 4) Telephone(s) may be used.
| Personnel: | [6 empty] | 11 x persons (including lecturer). Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 19.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | For flexibility in use, direct access to a store is required. The call repeat lamp is situated over the door outside the room. The following items may be provided: - a TV; - an overhead projector; - video-conferencing facilities; - an induction loop hearing system; - a public address system (in larger seminar rooms); - a clinical wash-hand basin and gel dispenser to allow for clinical use of the room; - audiovisual links to clinical areas for training purposes; - shelving, desks/tables and computers for training use. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
H1304-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | H1304-01 |  |  |  |  | Seminar room: 10 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 100-150 |  | On floor
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 300 |  | Over working plane
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 52
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 52 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | H1304-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | H1304-01 |  |  |  |  | Seminar room: 10 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control. Blinds will be required to darken room, full blackout is rarely required Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | H1304-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | H1304-01 |  |  |  |  | Seminar room: 10 places (including 1 wheelchair place)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 12 |  |  | 12 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT004 |  | OUTLET cable, fused, 13 amp, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 10 |  |  | 10 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT135 |  | SOCKET outlet, computer data, single, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SCR043 |  | SCREEN, projection, ceiling mounted, 1800H 1800W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA006 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 1200H1800W | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | PRO026 |  | PROJECTOR, multi-media, ceiling mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA051 |  | BOARD, flip chart, height adjustable, freestanding | [16 empty] | 3
| 10 |  |  | 10 |  |  |  |  | CHA318 |  | CHAIR, upright, with arms, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP036 |  | CUPBOARD, steel, 2 adjustable shelves, 2 door, lockable, 900H 900W 420D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB008 |  | TABLE, 710H 1200W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | J0232
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J0232 |  |  |  |  | Reception: 2 person
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception and registration of patients. 2) Maintaining appointments and attendance register. 3) Computer workstation(s) may be used. 4) Dealing with enquiries. 5) Telephone(s) may be used. 6) Controlling access to clinical or work area. 7) Staff notices, information and/or messages may be displayed.
| Personnel: | [6 empty] | 2 x staff. 2 x patients/visitors.
| Planning Relationships: | [5 empty] | Close to, with clear view of, entrance and waiting area. Close to self-registration point when provided. Close to clinical or work area(s). Easy access to records store when paper records are still used. Access to a "safe haven" area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 11 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | The reception desk should be accessible to all users and provide security for staff. In facilities for children and young people it should be child friendly. The following items may be provided: - a printer; - a "controlled entry" system; - a "next patient" call system; . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
J0232
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J0232 |  |  |  |  | Reception: 2 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 500 |  | Over desk task area
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 58
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 58 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | J0232
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J0232 |  |  |  |  | Reception: 2 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | J0232
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J0232 |  |  |  |  | Reception: 2 person
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | COU087 |  | COUNTER RECEPTION, console top, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PAN063 |  | PANEL, indicator | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | J0232-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J0232-01 |  |  |  |  | Reception: 1 person
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception and registration of patients. 2) Maintaining appointments and attendance register. 3) Computer workstation(s) may be used. 4) Dealing with enquiries. 5) Telephone(s) may be used. 6) Controlling access to clinical or work area. 7) Staff notices, information and/or messages may be displayed.
| Personnel: | [6 empty] | 1 x staff. 1 x patients/visitors.
| Planning Relationships: | [5 empty] | Close to, with clear view of, entrance and waiting area. Close to self-registration point when provided. Close to clinical or work area(s). Easy access to records store when paper records are still used. Access to a "safe haven" area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8.5 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | The reception desk should be accessible to all users and provide security for staff. In facilities for children and young people it should be child friendly. The following items may be provided: - a printer; - a "controlled entry" system; - a "next patient" call system; . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
J0232-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J0232-01 |  |  |  |  | Reception: 1 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 500 |  | Over desk task area
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 59
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 59 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | J0232-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J0232-01 |  |  |  |  | Reception: 1 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | J0232-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J0232-01 |  |  |  |  | Reception: 1 person
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | COU090 |  | COUNTER RECEPTION, console top, 1 place | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PAN063 |  | PANEL, indicator | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | J0232-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J0232-02 |  |  |  |  | Reception: 3 person
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception and registration of patients. 2) Maintaining appointments and attendance register. 3) Computer workstation(s) may be used. 4) Dealing with enquiries. 5) Telephone(s) may be used. 6) Controlling access to clinical or work area. 7) Staff notices, information and/or messages may be displayed.
| Personnel: | [6 empty] | 3 x staff. 3 x patients/visitors.
| Planning Relationships: | [5 empty] | Close to, with clear view of, entrance and waiting area. Close to self-registration point when provided. Close to clinical or work area(s). Easy access to records store when paper records are still used. Access to a "safe haven" area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 14.5 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | The reception desk should be accessible to all users and provide security for staff. In facilities for children and young people it should be child friendly. The following items may be provided: - a printer; - a "controlled entry" system; - a "next patient" call system; . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
J0232-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J0232-02 |  |  |  |  | Reception: 3 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 500 |  | Over desk task area
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 60
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 60 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | J0232-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J0232-02 |  |  |  |  | Reception: 3 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | J0232-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J0232-02 |  |  |  |  | Reception: 3 person
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | COU095 |  | COUNTER RECEPTION, console top, 3 place | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PAN063 |  | PANEL, indicator | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | J1155
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1155 |  |  |  |  | Waiting area: 20 places (including 2 wheelchair places)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patients, relatives and escorts wait to be seen. 2) Displaying information.
| Personnel: | [6 empty] | 20 x persons, including 2 x wheelchair user
| Planning Relationships: | [5 empty] | Adjacent to reception area. Close to clinical or work area. Close to WC facilities.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 30 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Type of seating to be suitable for patient profile. Method for calling patients into clinical rooms to be decided locally. The following items may be provided: - an enclosed noticeboard; - background music and other entertainment facilities; - television and internet access.
| ADB | [7 empty] | Room Environmental Data
J1155
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1155 |  |  |  |  | Waiting area: 20 places (including 2 wheelchair places)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | -
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 63
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 63 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | J1155
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1155 |  |  |  |  | Waiting area: 20 places (including 2 wheelchair places)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control or Not applicable Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | J1155
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1155 |  |  |  |  | Waiting area: 20 places (including 2 wheelchair places)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAC089 |  | RACK, leaflet/pamphlet, 4 sections, with adjustable dividers, wall mounted, 300H 805W 215D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | RAC091 |  | RACK, magazine, 3 shelves, floor standing, fixed to the wall, 1400H 900W 300D | [16 empty] | 2
| 3 |  |  | 3 |  |  |  |  | CHA367 |  | UNIT CHAIR, 1 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA368 |  | UNIT CHAIR, 2 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA369 |  | UNIT CHAIR, 3 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | J1155-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1155-01 |  |  |  |  | Waiting area: 15 places (including 1wheelchair place)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patients, relatives and escorts wait to be seen. 2) Displaying information.
| Personnel: | [6 empty] | 15 x persons, including 1 x wheelchair user.
| Planning Relationships: | [5 empty] | Adjacent to reception area. Close to clinical or work area. Close to WC facilities.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 22.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Type of seating to be suitable for patient profile. Method for calling patients into clinical rooms to be decided locally. The following items may be provided: - an enclosed noticeboard; - background music and other entertainment facilities; - television and internet access.
| ADB | [7 empty] | Room Environmental Data
J1155-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1155-01 |  |  |  |  | Waiting area: 15 places (including 1wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | -
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 64
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 64 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | J1155-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1155-01 |  |  |  |  | Waiting area: 15 places (including 1wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control or Not applicable Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | J1155-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1155-01 |  |  |  |  | Waiting area: 15 places (including 1wheelchair place)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAC089 |  | RACK, leaflet/pamphlet, 4 sections, with adjustable dividers, wall mounted, 300H 805W 215D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | RAC091 |  | RACK, magazine, 3 shelves, floor standing, fixed to the wall, 1400H 900W 300D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CHA367 |  | UNIT CHAIR, 1 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA368 |  | UNIT CHAIR, 2 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA369 |  | UNIT CHAIR, 3 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | J1255
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1255 |  |  |  |  | Waiting area: 5 places (including 1 wheelchair place)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patients, relatives and escorts wait to be seen. 2) Displaying information.
| Personnel: | [6 empty] | 5 x persons, including 1 x wheelchair user
| Planning Relationships: | [5 empty] | Close to clinical or work area. Close to WC facilities.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 9 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design. .
| Notes: | [7 empty] | Type of seating to be suitable for patient profile. Method for calling patients into clinical rooms to be decided locally. The following items may be provided: - an enclosed noticeboard; - background music and other entertainment facilities; - television and internet access.
| ADB | [7 empty] | Room Environmental Data
J1255
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1255 |  |  |  |  | Waiting area: 5 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | -
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 65
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 65 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | J1255
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1255 |  |  |  |  | Waiting area: 5 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control or Not applicable Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | J1255
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1255 |  |  |  |  | Waiting area: 5 places (including 1 wheelchair place)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAC089 |  | RACK, leaflet/pamphlet, 4 sections, with adjustable dividers, wall mounted, 300H 805W 215D | [16 empty] | 2
| 4 |  |  | 4 |  |  |  |  | CHA367 |  | UNIT CHAIR, 1 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | J1255-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1255-01 |  |  |  |  | Waiting area: 10 places (including 1 wheelchair place)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patients, relatives and escorts wait to be seen. 2) Displaying information.
| Personnel: | [6 empty] | 10 x persons, including 1 x wheelchair user.
| Planning Relationships: | [5 empty] | Close to clinical or work area. Close to WC facilities.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 15 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | Type of seating to be suitable for patient profile. Method for calling patients into clinical rooms to be decided locally. The following items may be provided: - an enclosed noticeboard; - background music and other entertainment facilities; - television and internet access.
| ADB | [7 empty] | Room Environmental Data
J1255-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1255-01 |  |  |  |  | Waiting area: 10 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | -
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 66
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 66 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | J1255-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1255-01 |  |  |  |  | Waiting area: 10 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control or Not applicable Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | J1255-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1255-01 |  |  |  |  | Waiting area: 10 places (including 1 wheelchair place)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAC089 |  | RACK, leaflet/pamphlet, 4 sections, with adjustable dividers, wall mounted, 300H 805W 215D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | RAC091 |  | RACK, magazine, 3 shelves, floor standing, fixed to the wall, 1400H 900W 300D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CHA367 |  | UNIT CHAIR, 1 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA368 |  | UNIT CHAIR, 2 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA369 |  | UNIT CHAIR, 3 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | J1414
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1414 |  |  |  |  | Play area: 3 children
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Children accompanying relatives or waiting to be seen are able to play. 2) Toys, books and games are stored.
| Personnel: | [6 empty] | 3 x children
| Planning Relationships: | [5 empty] | Off, and observable from, the waiting area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 4.5 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
J1414
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1414 |  |  |  |  | Play area: 3 children
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/EM
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 68
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 68 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | J1414
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1414 |  |  |  |  | Play area: 3 children
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control. Window opening restrictors max 100mm at bottom Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Desirable - Project Option Clear safety glass when provided Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | J1414
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1414 |  |  |  |  | Play area: 3 children
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BIN007 |  | BIN, storage, complete with drop on lid, mobile, 550H 610W 510D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA335 |  | CHAIR, child, upright, stacking, seat height 380, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB060 |  | TABLE, child, 470H 1200W 700D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | J1414-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1414-01 |  |  |  |  | Play area: 5 children
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Children accompanying relatives or waiting to be seen are able to play. 2) Toys, books and games are stored.
| Personnel: | [6 empty] | 5 x children.
| Planning Relationships: | [5 empty] | Off, and observable from, the waiting area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 7.5 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
J1414-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1414-01 |  |  |  |  | Play area: 5 children
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/EM
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 69
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 69 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | J1414-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1414-01 |  |  |  |  | Play area: 5 children
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control. Window opening restrictors max 100mm at bottom Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Desirable - Project Option Clear safety glass when provided Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | J1414-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | J1414-01 |  |  |  |  | Play area: 5 children
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BIN007 |  | BIN, storage, complete with drop on lid, mobile, 550H 610W 510D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA335 |  | CHAIR, child, upright, stacking, seat height 380, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB060 |  | TABLE, child, 470H 1200W 700D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | K0303
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | K0303 |  |  |  |  | Maintenance: workshop Radiology
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Maintaining radiodiagnostic equipment including TV and VDTs. 2) Tools and equipment are stored. 3) Equipment may be serviced or repaired. 4) Manoeuvring mobile x-ray film trolley. 5) Hand washing.
| Personnel: | [6 empty] | 03 x Staff Intermittent use
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 11 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Should work involving the generation of X-rays take place in this space suitable Radiological protection measures must be adopted with statutory warning signs. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
K0303
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | K0303 |  |  |  |  | Maintenance: workshop Radiology
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or +ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 500 |  | Over task area
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 71
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 71 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Heat detection dependant on activities
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | K0303
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | K0303 |  |  |  |  | Maintenance: workshop Radiology
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | K0303
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | K0303 |  |  |  |  | Maintenance: workshop Radiology
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS106 |  | BASIN, medium, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT206 |  | SOCKET outlet television aerial, single. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC063 |  | CABINET, base, modular storage, for 600 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC065 |  | CABINET, base, modular storage, for 600 facing inserts, with 3 drawers, on plinth, 900H | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC073 |  | CABINET, upper, modular storage, for 600 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WOR089 |  | WORKTOP, heavy duty, 3000W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL004 |  | HOLDER, sack, with lid foot operated, small, freestanding | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STO007 |  | STOOL, metal frame, upholstered, 710 height | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | WOR009 |  | WORKBENCH, engineer, heavy duty steel plate, complete with relevant components, 840H 1800W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | K0901
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | K0901 |  |  |  |  | Machine room: technician equipment room No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
Activities:
| Personnel: | [6 empty] | 1 - 2 x Person Intermittent use
| Planning Relationships: | [5 empty] | Good access for plant and equipment.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 16 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Equipment to be project specific; depending on equipment type and manufacturer.
| ADB | [7 empty] | Room Environmental Data
K0901
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | K0901 |  |  |  |  | Machine room: technician equipment room No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 20
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
Type Of Control:
Daytime General Service Illuminance (Lux):
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 79
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 79 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Heat detection dependant on activities
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | K0901
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | K0901 |  |  |  |  | Machine room: technician equipment room No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | K0901
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | K0901 |  |  |  |  | Machine room: technician equipment room No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Clinical administration. 2) Computer workstation(s) may be used. 3) Telephone(s) may be used. 4) Discussions and interviews may take place. 5) Files and records are stored. 6) Hanging outdoor clothing. 7) Secure holding/storing of clothing and personal belongings. 8) Printer may be used. 9) Electronic patient records (EPRs) may be accessed and updated. 10) Staff notices, information and/or messages may be displayed. 11) Dealing with enquiries. 12) Information on computers may be accessed.
| Personnel: | [6 empty] | 1 x staff Up to x 2 others.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following equipment is shown on the room layout but is optional: - call repeat lamps for controlled drugs cupboards (but required if the office is used for clinical control). The following items may provided; - shelving; - printer. The following items may be provided if the office is used for clinical control: - a small safe; - a key cupboard; - an alarm panel, see HTM 08-03; - a dimming switch - recommended if the room is used for viewing digital images. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 3 |  |  | 3 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG138 |  | LUMINAIRE, indicating controlled drugs cupboard repeat | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB049 |  | CABINET, lateral filing, 6 rails, 2 door, 1970H 1000W 470D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DES026 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1400W 700D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA057 |  | DRAWER UNIT, 3 drawer, lockable, on castors, desk height 715H 430W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0252-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0252-02 |  |  |  |  | Office: 3 person
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Clinical administration. 2) Computer workstation(s) may be used. 3) Telephone(s) may be used. 4) Discussions and interviews may take place. 5) Files and records are stored. 6) Hanging outdoor clothing. 7) Secure holding/storing of clothing and personal belongings.
| Personnel: | [6 empty] | 3 x staff. Up to 3 x others.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 18 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following equipment is shown on the room layout but is optional: - call repeat lamps for controlled drugs cupboards (but required if the office is used for clinical control). The following items may be provided if the office is used for clinical control: - a dimming switch - recommended if the room is used for viewing digital images. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0252-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0252-02 |  |  |  |  | Office: 3 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0252-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0252-02 |  |  |  |  | Office: 3 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0252-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0252-02 |  |  |  |  | Office: 3 person
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 5 |  |  | 5 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG138 |  | LUMINAIRE, indicating controlled drugs cupboard repeat | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB049 |  | CABINET, lateral filing, 6 rails, 2 door, 1970H 1000W 470D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | DES026 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1400W 700D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | DRA057 |  | DRAWER UNIT, 3 drawer, lockable, on castors, desk height 715H 430W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0254
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0254 |  |  |  |  | Office: 4 person
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Clinical administration. 2) Computer workstation(s) may be used. 3) Telephone(s) may be used. 4) Files and records are stored. 5) Hanging outdoor clothing. 6) Secure holding/storing of clothing and personal belongings. 7) Printer may be used. 8) Electronic patient records (EPRs) may be accessed and updated. 9) Information on computers may be accessed. 10) Staff notices, information and/or messages may be displayed.
| Personnel: | [6 empty] | 4 x staff. Up to 4 x others.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 24 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The following equipment is shown on the room layout but is optional: - call repeat lamps for controlled drugs cupboards (but required if the office is used for clinical control). The following items may be provided if the office is used for clinical control: - a dimming switch - recommended if the room is used for viewing digital images. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0254
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0254 |  |  |  |  | Office: 4 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0254
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0254 |  |  |  |  | Office: 4 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0254
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0254 |  |  |  |  | Office: 4 person
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 5 |  |  | 5 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG138 |  | LUMINAIRE, indicating controlled drugs cupboard repeat | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CAB049 |  | CABINET, lateral filing, 6 rails, 2 door, 1970H 1000W 470D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | DES026 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1400W 700D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | DRA057 |  | DRAWER UNIT, 3 drawer, lockable, on castors, desk height 715H 430W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0278-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0278-01 |  |  |  |  | Administration area: shared use: 4 workstations
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Clinical administration. 2) Computer workstation(s) may be used. 3) Telephone(s) may be used. 4) Files and records are stored. 5) Secure holding/storing of clothing and personal belongings.
| Personnel: | [6 empty] | 4 x staff. Up to 2 x others.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 20 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The layout illustrates socket outlets at desk height because they should be easily accessible to enable equipment to be switched off for energy conservation. Floor box services are discouraged as they make it harder to convert the space into a clinical room in the future. It is therefore assumed that the workstations are wire managed. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0278-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0278-01 |  |  |  |  | Administration area: shared use: 4 workstations
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0278-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0278-01 |  |  |  |  | Administration area: shared use: 4 workstations
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0278-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0278-01 |  |  |  |  | Administration area: shared use: 4 workstations
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 4 |  |  | 4 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | DES026 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1400W 700D | [16 empty] | 3
| 12 |  |  | 12 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | DRA057 |  | DRAWER UNIT, 3 drawer, lockable, on castors, desk height 715H 430W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0278-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0278-02 |  |  |  |  | Administration area: shared use: 6 workstations
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Clinical administration. 2) Computer workstation(s) may be used. 3) Telephone(s) may be used. 4) Files and records are stored. 5) Secure holding/storing of clothing and personal belongings. 6) Hanging outdoor clothing. 7) Information on computers may be accessed. 8) Printer may be used. 9) Electronic patient records (EPRs) may be accessed and updated. 10) Staff notices, information and/or messages may be displayed. 11) Dealing with enquiries. 12) Patient records may be reviewed and recorded. 13) Shredding documents.
| Personnel: | [6 empty] | 6 x staff. Up to 3 x others.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 30 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The layout illustrates socket outlets at desk height because they should be easily accessible to enable equipment to be switched off for energy conservation. Floor box services are discouraged as they make it harder to convert the space into a clinical room in the future. It is therefore assumed that the workstations are wire managed. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0278-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0278-02 |  |  |  |  | Administration area: shared use: 6 workstations
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0278-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0278-02 |  |  |  |  | Administration area: shared use: 6 workstations
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0278-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0278-02 |  |  |  |  | Administration area: shared use: 6 workstations
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 12 |  |  | 12 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SCR026 |  | SCREEN, dividing, 1500H 2000W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 6 |  |  | 6 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | DES026 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1400W 700D | [16 empty] | 3
| 18 |  |  | 18 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | DRA057 |  | DRAWER UNIT, 3 drawer, lockable, on castors, desk height 715H 430W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0326-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0326-01 |  |  |  |  | Office: technical and data review: 2 workstations
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Stored data and/or images may be archived, retrieved or distributed. 2) Test reports may be prepared. 3) Electronic patient records (EPRs) may be accessed and updated. 4) Staff notices, information and/or messages may be displayed. 5) Telephone(s) may be used.
| Personnel: | [6 empty] | 2 x staff. 1 x other.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | A dimming switch is recommended if the room is used for viewing digital images. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0326-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0326-01 |  |  |  |  | Office: technical and data review: 2 workstations
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0326-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0326-01 |  |  |  |  | Office: technical and data review: 2 workstations
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0326-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0326-01 |  |  |  |  | Office: technical and data review: 2 workstations
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 3 |  |  | 3 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | WRT065 |  | WORKTOP, non-clinical, 1500W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB027 |  | CABINET, filing, 2 drawer, 710H 800W 470D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0410
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0410 |  |  |  |  | Photocoping/printing room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Carrying out printing activities. 2) Carrying out photocopying activities. 3) Shredding documents. 4) Stationery/paper is stored.
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Within an administration space.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 6 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | One photocopy/printing room, with multifunctional printer/copier and storage for paper/printing supplies, for every 32 workstations. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0410
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0410 |  |  |  |  | Photocoping/printing room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0410
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0410 |  |  |  |  | Photocoping/printing room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0410
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0410 |  |  |  |  | Photocoping/printing room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP036 |  | CUPBOARD, steel, 2 adjustable shelves, 2 door, lockable, 900H 900W 420D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | PRI010 |  | PRINTER multifunction, network, floor standing | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SHR001 |  | SHREDDER, paper | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0724
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0724 |  |  |  |  | Interview room: 4 places (including 1 wheelchair place)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Discussions and interviews may take place. 2) Telephone(s) may be used. 3) Laptop computer(s) may be used. 4) Call systems may be used.
| Personnel: | [6 empty] | Up to 4 x persons.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items are shown on the room layout but are optional: - staff emergency call (not required if the room is for staff use only); - telephone (should not be provided in rooms intended as quiet spaces); - room in use switch and indicator. The following items may be provided: - a clinical wash-hand basin and gel dispenser to allow for clinical use of the room; . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0724
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0724 |  |  |  |  | Interview room: 4 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0724
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0724 |  |  |  |  | Interview room: 4 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0724
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0724 |  |  |  |  | Interview room: 4 places (including 1 wheelchair place)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG073 |  | ILLUMINATED SIGN, 'Room in use' | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC076 |  | SWITCH, 'Room in use' illuminated sign. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0727
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0727 |  |  |  |  | Interview room: 7 places (including 1 wheelchair place)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Discussions and interviews may take place. 2) Telephone(s) may be used. 3) Laptop computer(s) may be used. 4) Call systems may be used.
| Personnel: | [6 empty] | Up to 7 x persons.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items are shown on the room layout but are optional: - staff emergency call (not required if the room is for staff use only); - telephone (should not be provided in rooms intended as quiet spaces); - room in use switch and indicator. The following items may be provided: - a clinical wash-hand basin and gel dispenser to allow for clinical use of the room; . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0727
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0727 |  |  |  |  | Interview room: 7 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0727
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0727 |  |  |  |  | Interview room: 7 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0727
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M0727 |  |  |  |  | Interview room: 7 places (including 1 wheelchair place)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG073 |  | ILLUMINATED SIGN, 'Room in use' | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC076 |  | SWITCH, 'Room in use' illuminated sign. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA311 |  | SOFA CHAIR, 2 seater, easy, with arms, fully upholstered, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M1707
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M1707 |  |  |  |  | Duty room: 2 porters
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Waiting by duty porters. 2) Telephone(s) may be used. 3) Storing protective clothing.
| Personnel: | [6 empty] | 2 x Staff
| Planning Relationships: | [5 empty] | Located in the main entrance lobby.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M1707
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M1707 |  |  |  |  | Duty room: 2 porters
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 30 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M1707
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M1707 |  |  |  |  | Duty room: 2 porters
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M1707
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M1707 |  |  |  |  | Duty room: 2 porters
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LOC005 |  | LOCKER clothes, single, 1800H 300W 550D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB179 |  | TABLE, 720H 900W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M1713
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M1713 |  |  |  |  | Duty room: 6 porters
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Waiting by duty porters. 2) Telephone may be used and messages taken.
| Personnel: | [6 empty] | Up to 6 staff
| Planning Relationships: | [5 empty] | Near to main entrance lobby. Close to trolley/wheelchair park.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 10 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M1713
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M1713 |  |  |  |  | Duty room: 6 porters
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 30 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M1713
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M1713 |  |  |  |  | Duty room: 6 porters
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M1713
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | M1713 |  |  |  |  | Duty room: 6 porters
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 7 |  |  | 7 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA037 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 900H 1200W | [16 empty] | 2
| 6 |  |  | 6 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA363 |  | CHAIR, height adjustable, with arms, high back, swivel, 5 star base, wipeable, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DES006 |  | DESK, cantilever, single pedestal 3 drawer, modesty panel, 1200W 750D | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | LOC005 |  | LOCKER clothes, single, 1800H 300W 550D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB008 |  | TABLE, 710H 1200W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | N0219
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | N0219 |  |  |  |  | Scrub-up and gowning bay: 2 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Staff are able to scrub up within sight of clock. 2) Donning a sterile gown and gloves. 3) Dispensing disposable gloves. 4) Holding/storing protective sterile clothing and gloves.
| Personnel: | [6 empty] | Up to 3 staff.
| Planning Relationships: | [5 empty] | The scrub-up and gowning bay is intended as a recess off the treatment room or operating theatre.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 7 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | The following items are shown on the room layout but are optional: - shelving which may be replaced by a supplies trolley with or without a top for opening gowning packs. The following items may be provided: - sterile glove dispenser, assume to be stored on the shelving but may be located in a wall mounted dispenser; - lead apron rack.
| ADB | [7 empty] | Room Environmental Data
N0219
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | N0219 |  |  |  |  | Scrub-up and gowning bay: 2 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Duct mounted on Supply
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | N0219
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | N0219 |  |  |  |  | Scrub-up and gowning bay: 2 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. Not applicable or 1 doorset: 1 x personnel access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | N0219
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | N0219 |  |  |  |  | Scrub-up and gowning bay: 2 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SHE212 |  | SHELF, 900W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRO602 |  | TROUGH scrub-up, hospital pattern, stainless steel, double, 75mm upstand, 950H 1600W 450D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS006 |  | DISPENSER, disposable nailbrush, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | N0307
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | N0307 |  |  |  |  | Anaesthetic bay: 1 patient trolley
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may arrive on a trolley. 2) Administration of general anaesthetic. 3) Maintenance of general anaesthesia. 4) Anaesthetic accessories and equipment are stored. 5) Controlled and scheduled drugs are stored securely. 6) Holding sterile supplies. 7) Holding/storing stock of infusion fluids. 8) Statutory notices. may be displayed 9) Recording patient data/notes. 10) Collecting waste materials for disposal. 11) Clinical hand washing.
| Personnel: | [6 empty] | 1 x Patient 4 x Staff
| Planning Relationships: | [5 empty] | In Imaging: En-suite Special Procedures Radiodiagnostic Rooms served. In Cardiac: En-suite Catheter Laboratory.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 10 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Lamp indicator call & controlled drugs cupboard should be sited outside the entrance of the room. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
N0307
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | N0307 |  |  |  |  | Anaesthetic bay: 1 patient trolley
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 1000
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Duct mounted on Supply
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | N0307
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | N0307 |  |  |  |  | Anaesthetic bay: 1 patient trolley
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | N0307
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | N0307 |  |  |  |  | Anaesthetic bay: 1 patient trolley
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL035 |  | LAMP repeat call (patient/staff or staff emergency or Cardiac call), ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG053 |  | LUMINAIRE, examination, ceiling, adjustable, 1000 lux | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC503 |  | PHARMACY CABINET, 600mm facing, with 4 shelves, 1 pull out prep. shelf, controlled drugs cupboard, warning light, 1 door hinged right w/security safe lock, o/a height 1200 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT004 |  | OUTLET cable, fused, 13 amp, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT050 |  | OUTLET, controlled drugs cupboard | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT056 |  | CONNECTION UNIT, unswitched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT461 |  | OUTLET, nitrous oxide, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT480 |  | OUTLET, gas scavenging (AGS), medical | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SMC063 |  | CABINET, base, modular storage, for 600 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC073 |  | CABINET, upper, modular storage, for 600 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW034 |  | WORKTOP, clinical, for 600 facing modular storage cabinets, 2400W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SUC001 |  | SUCTION UNIT, pipeline, high/low pressure, rail/wall mounted | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRA110 |  | TRACK, curtain, one sided, 3600mm length | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | N0307
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | N0307 |  |  |  |  | Anaesthetic bay: 1 patient trolley
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF091 |  | REFRIGERATOR, drug, capacity 35 litre, external temperature gauge, lockable, wall mounted, 510H 380W 445D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | ANA001 |  | ANAESTHETIC MACHINE/WORKSTATION electrically powered piston ventilator, mobile, 1350H 750W 650D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STA142 |  | STAND, infusion, twin hook, breaks, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STO006 |  | STOOL, surgeon/anaesthetist, height adjustable, includes anti-static seat pads | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO281 |  | TROLLEY PATIENT, with brakes, 800H 2050W 550D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | N0310
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | N0310 |  |  |  |  | Anaesthetic and recovery bay: 1 MRI trolley, 1 patient trolley space, 1 resuscitation trolley
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may arrive on foot in a wheelchair or on a trolley 2) Patient may arrive on a trolley or in a bed. 3) Positioning patient on MRI trolley. 4) Administration of IV sedation. 5) Administration of general anaesthetic using MRI-compatible equipment. 6) Maintenance of general anaesthesia. 7) Anaesthetic accessories and equipment are stored. 8) Controlled and scheduled drugs are stored securely. 9) Holding sterile supplies. 10) Holding/storing stock of infusion fluids. 11) Post anaesthetic recovery of patients. 12) Observation is undertaken by medical and nursing staff. 13) Recording patient data/notes. 14) Statutory notices. may be displayed 15) Parking resuscitation trolley. 16) Clinical hand washing.
| Personnel: | [6 empty] | 1 x Patient 4 x Staff
| Planning Relationships: | [5 empty] | Convenient to MRI Scanner Room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 20 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Lamp indicator call and controlled drugs cupboard should be sited outside the entrance of the room. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
N0310
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | N0310 |  |  |  |  | Anaesthetic and recovery bay: 1 MRI trolley, 1 patient trolley space, 1 resuscitation trolley
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 1000
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
| Standby Lighting Grade - Local Lighting: | [13 empty] | A
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Duct mounted on Supply
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | N0310
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | N0310 |  |  |  |  | Anaesthetic and recovery bay: 1 MRI trolley, 1 patient trolley space, 1 resuscitation trolley
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | N0310
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | N0310 |  |  |  |  | Anaesthetic and recovery bay: 1 MRI trolley, 1 patient trolley space, 1 resuscitation trolley
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL035 |  | LAMP repeat call (patient/staff or staff emergency or Cardiac call), ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG053 |  | LUMINAIRE, examination, ceiling, adjustable, 1000 lux | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC503 |  | PHARMACY CABINET, 600mm facing, with 4 shelves, 1 pull out prep. shelf, controlled drugs cupboard, warning light, 1 door hinged right w/security safe lock, o/a height 1200 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT004 |  | OUTLET cable, fused, 13 amp, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT050 |  | OUTLET, controlled drugs cupboard | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT056 |  | CONNECTION UNIT, unswitched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT461 |  | OUTLET, nitrous oxide, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT480 |  | OUTLET, gas scavenging (AGS), medical | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SMC063 |  | CABINET, base, modular storage, for 600 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC073 |  | CABINET, upper, modular storage, for 600 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW034 |  | WORKTOP, clinical, for 600 facing modular storage cabinets, 2400W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SUC001 |  | SUCTION UNIT, pipeline, high/low pressure, rail/wall mounted | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRA110 |  | TRACK, curtain, one sided, 3600mm length | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | N0310
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | N0310 |  |  |  |  | Anaesthetic and recovery bay: 1 MRI trolley, 1 patient trolley space, 1 resuscitation trolley
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF091 |  | REFRIGERATOR, drug, capacity 35 litre, external temperature gauge, lockable, wall mounted, 510H 380W 445D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STO006 |  | STOOL, surgeon/anaesthetist, height adjustable, includes anti-static seat pads | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO283 |  | TROLLEY PATIENT, non-ferrous materials, full length tilt, adjustable head rest, side rails, 2075L 625D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO310 |  | TROLLEY, emergency/resuscitation, complete with defibrillator, 955H 825W 575D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | P0625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | P0625 |  |  |  |  | Pantry/refreshment area
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Preparing beverages/snacks with patients. 2) Microwave oven may be used. 3) Small amounts of dry goods are stored in cupboard(s). 4) Provision of refrigerated storage. 5) Trays, crockery and cutlery are stored. 6) Disposal of waste and contaminated materials. 7) Hand-rinse basin may be used.
| Personnel: | [6 empty] | 1 - 2 x persons. Intermittent use.
| Planning Relationships: | [5 empty] | Located in staff, patient or visitors areas as appropriate.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following items are included on the room layout but are optional: - a microwave oven; - a dishwasher. The layout is suitable for ambulant/semi-ambulant users, consideration must be given to wheelchair user provision.
| ADB | [7 empty] | Room Environmental Data
P0625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | P0625 |  |  |  |  | Pantry/refreshment area
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | -
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Heat
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | P0625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | P0625 |  |  |  |  | Pantry/refreshment area
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | P0625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | P0625 |  |  |  |  | Pantry/refreshment area
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS015 |  | BASIN, small, stainless steel, apron front, 1 tap hole, 500W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP703 |  | CUPBOARD, base, with door, on plinth, 900H 400W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP715 |  | CUPBOARD, base, including sink panel, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CUP731 |  | CUPBOARD/DRAWER UNIT, base, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CUP753 |  | CUPBOARD, upper, with door, 600H 600W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT301 |  | OUTLET, cold water for equipment | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT341 |  | OUTLET, drainage, anti-syphon | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP359 |  | TAP, pillar, high neck, long lever, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAT003 |  | WATER BOILER, 2.5 litre, electric, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WRT237 |  | WORKTOP, dished, stainless steel, with integral left of centre sink bowl and 2 tap holes, 3500W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS007 |  | DISPENSER, paper towel roll, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | WAS065 |  | DISHWASHER, under bench, high temperature | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | OVE013 |  | OVEN, microwave, heavy duty, 1600watt, capacity 26 litre, 370H 465W 560D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF058 |  | REFRIGERATOR, capacity 160 litre, automatic defrost, stainless steel, underbench, external temperature gauge, lockable, on castors, 850H 610W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | P0808
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | P0808 |  |  |  |  | Vending machines
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Buying cold snacks/beverages from vending machines.
| Personnel: | [6 empty] | Intermittent use.
| Planning Relationships: | [5 empty] | Adjacent to main waiting area. Adjacent to main entrance & concourse area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 3 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
P0808
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | P0808 |  |  |  |  | Vending machines
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | -
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | P0808
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | P0808 |  |  |  |  | Vending machines
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | P0808
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | P0808 |  |  |  |  | Vending machines
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT054 |  | CONNECTION UNIT, unswitched, 13 amp, neon indicator | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT301 |  | OUTLET, cold water for equipment | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | VEN001 |  | VENDING MACHINE, cold snacks | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | VEN002 |  | VENDING MACHINE, hot/cold drinks | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | P0811
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | P0811 |  |  |  |  | Drinking water dispenser
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Dispensing chilled water. 2) Disposal of used cups.
| Personnel: | [6 empty] | Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 0.5 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
P0811
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | P0811 |  |  |  |  | Drinking water dispenser
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | -
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 100
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | N
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | P0811
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | P0811 |  |  |  |  | Drinking water dispenser
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | P0811
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | P0811 |  |  |  |  | Drinking water dispenser
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT054 |  | CONNECTION UNIT, unswitched, 13 amp, neon indicator | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT315 |  | OUTLET, drinking water for equipment | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS002 |  | DISPENSER, cooler, drinking water, (capacity 63.3 l/hr), floor standing | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS012 |  | DISPENSER, disposable cup, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | S0012
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | S0012 |  |  |  |  | Infant feeding room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Mother breast or bottle feeding her baby. 2) Mother to express milk using breast pump. 3) Wash-hand basin may be used.
| Personnel: | [6 empty] | 1 x infant. 1 x parent/carer.
| Planning Relationships: | [5 empty] | Easy access from waiting area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 6 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | Expressed milk must be stored elsewhere.
| ADB | [7 empty] | Room Environmental Data
S0012
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | S0012 |  |  |  |  | Infant feeding room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E/N
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | S0012
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | S0012 |  |  |  |  | Infant feeding room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | S0012
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | S0012 |  |  |  |  | Infant feeding room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS107 |  | BASIN, medium, general pattern, vitreous china, 2 tap holes, no overflow, bottom outlet, 500W 400D. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA306 |  | CHAIR, easy, low back, with open arms, upholstered, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | T0211-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | T0211-01 |  |  |  |  | Staff communication base: 1 place
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Electronic patient records (EPRs) may be accessed and updated. 2) Computer workstation(s) may be used. 3) Dealing with enquiries. 4) Telephone(s) may be used. 5) Staff supervise and observe patients. 6) Carrying out administration and clerical duties. 7) Information may be provided to patients, carers and visitors. 8) Clinical administration. 9) Patient records may be reviewed and recorded. 10) Call systems may be used.
| Personnel: | [6 empty] | 1 x staff. 2 x other staff or patients/visitors.
| Planning Relationships: | [5 empty] | Situated to allow easy access and good observation of the areas served. Access to a "safe haven" area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8.5 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | Clear access space around the staff communication base should be maintained even when someone is standing at the front of the base. The following items are shown on the room layout but are optional: - call system alarm panel, see HTM 08-03; The following items may be provided: - controlled drugs cupboard alarm; - departmental controlled entry system. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
T0211-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | T0211-01 |  |  |  |  | Staff communication base: 1 place
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
| Nighttime General Service Illuminance (Lux): | [13 empty] | 30-200
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
| Standby Lighting Grade - Local Lighting: | [13 empty] | A
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | T0211-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | T0211-01 |  |  |  |  | Staff communication base: 1 place
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | T0211-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | T0211-01 |  |  |  |  | Staff communication base: 1 place
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | COU090 |  | COUNTER RECEPTION, console top, 1 place | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PAN063 |  | PANEL, indicator | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | T0516
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | T0516 |  |  |  |  | Clean utility: barium preparation
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Storing contrast media - barium suspensions and powders. 2) Sterile equipment, consumable supplies and packs are stored. 3) Non-sterile medical items, equipment and supplies are stored. 4) Miscellaneous equipment is stored. 5) Storing glassware. 6) Preparation of intravenous fluids for infusion. 7) Trolleys for clinical procedures are prepared and laid up. 8) Washing containers. 9) Clinical hand washing. 10) Moving/manoeuvring trolley(s). 11) Equipment trolley(s) may be parked and/or stored.
| Personnel: | [6 empty] | 02 x Staff Intermittent use
| Planning Relationships: | [5 empty] | Close to Fluoroscopy.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 5.5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | Drainage to be suitable for disposal of barium.
| ADB | [7 empty] | Room Environmental Data
T0516
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | T0516 |  |  |  |  | Clean utility: barium preparation
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 150
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
| Standby Lighting Grade - Local Lighting: | [13 empty] | B
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | T0516
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | T0516 |  |  |  |  | Clean utility: barium preparation
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | T0516
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | T0516 |  |  |  |  | Clean utility: barium preparation
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC063 |  | CABINET, base, modular storage, for 600 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW053 |  | WORKTOP, clinical, for 3 x 400 facing modular storage cabinets, 1365W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SNS757 |  | SINKTOP, single bowl, no tap holes, no overflow, right hand integral ribbed drainer, stainless steel, 1200W 650D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP359 |  | TAP, pillar, high neck, long lever, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS007 |  | DISPENSER, paper towel roll, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL004 |  | HOLDER, sack, with lid foot operated, small, freestanding | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | T0522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | T0522 |  |  |  |  | Preparation room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Trays are prepared and trolleys laid up for surgical/clinical procedures. 2) Sterile pre-set trays are held/stored 3) Sterile equipment, consumable supplies and packs are stored. 4) Non-sterile medical items, equipment and supplies are stored. 5) Sterile fluids are stored. 6) Instrument trolleys are held/stored. 7) Storing sundries and small items.
| Personnel: | [6 empty] | 2-3 x staff.
| Planning Relationships: | [5 empty] | Direct access to operating theatre. Access from corridor for delivery of supplies.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The number and size of dressing/instrument trolleys is a project team option. The following items are shown on the room layout but are optional: - heated lotion cabinet which could be provided in a central store instead of within the preparation room. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
T0522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | T0522 |  |  |  |  | Preparation room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | >25
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | 35 pascals
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40 |  | The LAmax,f dB noise limit applies at any time.
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | 50
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | T0522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | T0522 |  |  |  |  | Preparation room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control, security control as necessary, see BS2881 Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | T0522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | T0522 |  |  |  |  | Preparation room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SMC051 |  | CABINET, tall, modular storage, for 600 facing inserts, open, on plinth, 2100H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW025 |  | WORKTOP, clinical, for 600 facing modular storage cabinets, 1500W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAB036 |  | CABINET warming, lotion, 48x1 litre, 1320H 620W 630D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SMF011 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 465D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STA102 |  | STAND, 2 lotion bowls, stainless steel, (Bowls not included). | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO133 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 750W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO201 |  | TROLLEY, instruments, stainless steel, buffered, 870H 920W 620D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | T0535
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | T0535 |  |  |  |  | Clean utility room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Dressing/instrument trolleys are held and prepared. 2) Sterile supplies and consumables are held. 3) Controlled and scheduled drugs are stored securely. 4) Non-controlled medicines and pharmaceuticals are stored securely. 5) Infusion fluids are stored. 6) Provision of refrigerated storage. 7) Flammable medicines are stored. 8) Supplies trolleys are held/stored. 9) Clinical wash-hand basin may be used. 10) Bar coded items may be tracked. 11) Medication is prepared for administration. 12) Contrast media, I.V. injections and other sterile procedures may be prepared. 13) Trolleys for clinical procedures are prepared and laid up. 14) Sterile packs, lotions and drugs may be prepared for immediate use. 15) Computer workstation(s) may be used.
| Personnel: | [6 empty] | 2 x staff.
| Planning Relationships: | [5 empty] | Close to clinical area, particularly treatment rooms.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 16 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | See BS 2881 for requirements for medicines storage. See Misuse of Drugs (Safe Custody) Regulations for requirements for scheduled/controlled drugs storage. The following items may be provided: - a barcode reader and charger. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
T0535
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | T0535 |  |  |  |  | Clean utility room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 150
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | T0535
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | T0535 |  |  |  |  | Clean utility room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control, security control as necessary, see BS2881 Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | T0535
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | T0535 |  |  |  |  | Clean utility room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT050 |  | OUTLET, controlled drugs cupboard | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT056 |  | CONNECTION UNIT, unswitched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC003 |  | CABINET, tall, modular storage, for 400 facing inserts, with door, on plinth, 2100H | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC023 |  | CABINET, upper, modular storage, for 400 facing inserts, with door, 750H | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC051 |  | CABINET, tall, modular storage, for 600 facing inserts, open, on plinth, 2100H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW056 |  | WORKTOP, clinical, for 6 x 400 facing modular storage cabinets, 2730W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAB064 |  | CABINET, metal, controlled drugs, 1 door, lockable, with warning light, wall mounted, 550H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | SMF011 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 465D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP550 |  | CUPBOARD, flammable material, metal, adjustable spillage tray and sump, lockable, 712H 355W 305D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF059 |  | REFRIGERATOR, medical (drug/vaccine), capacity 160 litre, external temperature gauge, automatic defrost, lockable, underbench, 850H 550W 620D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT011 |  | TROLLEY, modular storage, single open frame, including handles, with up to 10 sets of runners for 400 facing inserts, 1500H 600W 650D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0554
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0554 |  |  |  |  | Staff communal changing room: 20 lockers
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) User may undress and dress. 2) Changing into clean uniforms (including blues or greens). 3) Changing footwear. 4) Secure hanging of wet outdoor clothing. 5) Secure holding/storing of clothing and personal belongings. 6) Secure holding/storage of motorcycle and bicycle helmets. 7) Hanging outdoor clothing. 8) Disposal of dirty uniforms.
| Personnel: | [6 empty] | Up to 6 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Direct access to showers and/or individual changing room(s). Close to WCs. Close to uniform exchange, if provided.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 20 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | It is assumed that this space is supported by one individual changing room. See V0725 for details of semi-ambulant individual changing room and V0276 for independent wheelchair individual changing room. The room layout illustrates space for all users but includes lockers for generally ambulant users. A suitable number of lockers must comply with the requirements of BS8300/ADM for wheelchair users depending upon the expected user group. The following items may be provided: - cube lockers for personal belongings will be required if staff are not allocated their own changing lockers; - shaver sockets, shelves and lights associated with mirrors.
| ADB | [7 empty] | Room Environmental Data
V0554
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0554 |  |  |  |  | Staff communal changing room: 20 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0554
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0554 |  |  |  |  | Staff communal changing room: 20 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0554
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0554 |  |  |  |  | Staff communal changing room: 20 lockers
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 3 |  |  | 3 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | CHA383 |  | CHAIR, stacking, polypropylene, with back and seat pads, wipeable. | [16 empty] | 3
| 20 |  |  | 20 |  |  |  |  | LOC005 |  | LOCKER clothes, single, 1800H 300W 550D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC154 |  | RACK shoe, (bridge unit base between lockers assembly) 175H 1200W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAI023 |  | RAIL, coat hanging, 20 secure hangers with sleeve lock chain, (bridge unit top between lockers assembly), 1200W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0554-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0554-01 |  |  |  |  | Staff communal changing room: 5 lockers
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) User may undress and dress. 2) Changing into clean uniforms (including blues or greens). 3) Changing footwear. 4) Secure hanging of wet outdoor clothing. 5) Secure holding/storing of clothing and personal belongings. 6) Secure holding/storage of motorcycle and bicycle helmets. 7) Hanging outdoor clothing. 8) Disposal of dirty uniforms.
| Personnel: | [6 empty] | Up to 3 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Direct access to showers and/or individual changing room(s). Close to WCs. Close to uniform exchange, if provided.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | It is assumed that this space is supported by one individual changing room. See V0725 for details of semi-ambulant individual changing room and V0276 for independent wheelchair individual changing room. The room layout illustrates space for all users but includes lockers for generally ambulant users. A suitable number of lockers must comply with the requirements of BS8300/ADM for wheelchair users depending upon the expected user group. The following items may be provided: - cube lockers for personal belongings will be required if staff are not allocated their own changing lockers; - shaver sockets, shelves and lights associated with mirrors.
| ADB | [7 empty] | Room Environmental Data
V0554-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0554-01 |  |  |  |  | Staff communal changing room: 5 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0554-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0554-01 |  |  |  |  | Staff communal changing room: 5 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0554-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0554-01 |  |  |  |  | Staff communal changing room: 5 lockers
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CHA383 |  | CHAIR, stacking, polypropylene, with back and seat pads, wipeable. | [16 empty] | 3
| 5 |  |  | 5 |  |  |  |  | LOC005 |  | LOCKER clothes, single, 1800H 300W 550D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC158 |  | RACK shoe, (bridge unit base between lockers assembly) 175H 600W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAI026 |  | RAIL, coat hanging, 10 secure hangers with sleeve lock chain, (bridge unit top between lockers assembly), 600L | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0554-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0554-02 |  |  |  |  | Staff communal changing room: 10 lockers
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) User may undress and dress. 2) Changing into clean uniforms (including blues or greens). 3) Changing footwear. 4) Secure hanging of wet outdoor clothing. 5) Secure holding/storing of clothing and personal belongings. 6) Secure holding/storage of motorcycle and bicycle helmets. 7) Hanging outdoor clothing. 8) Disposal of dirty uniforms.
| Personnel: | [6 empty] | Up to 4 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Direct access to showers and/or individual changing room(s). Close to WCs. Close to uniform exchange, if provided.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 11 |  |  |  |  | Height (mm): |  |  |  | 2700
.
| Notes: | [7 empty] | It is assumed that this space is supported by one individual changing room. See V0725 for details of semi-ambulant individual changing room and V0276 for independent wheelchair individual changing room. The room layout illustrates space for all users but includes lockers for generally ambulant users. A suitable number of lockers must comply with the requirements of BS8300/ADM for wheelchair users depending upon the expected user group. The following items may be provided: - cube lockers for personal belongings will be required if staff are not allocated their own changing lockers; - shaver sockets, shelves and lights associated with mirrors.
| ADB | [7 empty] | Room Environmental Data
V0554-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0554-02 |  |  |  |  | Staff communal changing room: 10 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0554-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0554-02 |  |  |  |  | Staff communal changing room: 10 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0554-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0554-02 |  |  |  |  | Staff communal changing room: 10 lockers
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CHA383 |  | CHAIR, stacking, polypropylene, with back and seat pads, wipeable. | [16 empty] | 3
| 10 |  |  | 10 |  |  |  |  | LOC005 |  | LOCKER clothes, single, 1800H 300W 550D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC154 |  | RACK shoe, (bridge unit base between lockers assembly) 175H 1200W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAI023 |  | RAIL, coat hanging, 20 secure hangers with sleeve lock chain, (bridge unit top between lockers assembly), 1200W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0554-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0554-03 |  |  |  |  | Staff communal changing room: 30 lockers
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) User may undress and dress. 2) Changing into clean uniforms (including blues or greens). 3) Changing footwear. 4) Secure hanging of wet outdoor clothing. 5) Secure holding/storing of clothing and personal belongings. 6) Secure holding/storage of motorcycle and bicycle helmets. 7) Hanging outdoor clothing. 8) Disposal of dirty uniforms.
| Personnel: | [6 empty] | Up to 12 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Direct access to showers and/or individual changing room(s). Close to WCs. Close to uniform exchange, if provided.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 30 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | It is assumed that this space is supported by one individual changing room. See V0725 for details of semi-ambulant individual changing room and V0276 for independent wheelchair individual changing room. The room layout illustrates space for all users but includes lockers for generally ambulant users. A suitable number of lockers must comply with the requirements of BS8300/ADM for wheelchair users depending upon the expected user group. The following items may be provided: - cube lockers for personal belongings will be required if staff are not allocated their own changing lockers; - shaver sockets, shelves and lights associated with mirrors.
| ADB | [7 empty] | Room Environmental Data
V0554-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0554-03 |  |  |  |  | Staff communal changing room: 30 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0554-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0554-03 |  |  |  |  | Staff communal changing room: 30 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0554-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0554-03 |  |  |  |  | Staff communal changing room: 30 lockers
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 4 |  |  | 4 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | CHA383 |  | CHAIR, stacking, polypropylene, with back and seat pads, wipeable. | [16 empty] | 3
| 30 |  |  | 30 |  |  |  |  | LOC005 |  | LOCKER clothes, single, 1800H 300W 550D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | RAC154 |  | RACK shoe, (bridge unit base between lockers assembly) 175H 1200W 450D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | RAI023 |  | RAIL, coat hanging, 20 secure hangers with sleeve lock chain, (bridge unit top between lockers assembly), 1200W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0653
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0653 |  |  |  |  | Locker bay: 12 small lockers
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Secure holding/storing of clothing and personal belongings.
| Personnel: | [6 empty] | Intermittent use.
| Planning Relationships: | [5 empty] | Convenient to circulation route.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 1.5 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | Lockers included for generally ambulant users. A suitable number of lockers must comply with the requirements of BS8300/ADM for wheelchair users depending upon the expected user group.
| ADB | [7 empty] | Room Environmental Data
V0653
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0653 |  |  |  |  | Locker bay: 12 small lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 100-150
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0653
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0653 |  |  |  |  | Locker bay: 12 small lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0653
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0653 |  |  |  |  | Locker bay: 12 small lockers
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 3 |  |  | 3 |  |  |  |  | LOC014 |  | LOCKER, 4 compartments, 1800H 300W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Semi-ambulant person may undress/dress in privacy. 2) Hanging outdoor clothing. 3) Call systems may be used.
| Personnel: | [6 empty] | 1 x person. Intermittent use.
| Planning Relationships: | [5 empty] | Adjacent to sub-waiting area (if provided). Close to WC facilities. May be use in conjunction with staff changing area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items are shown on the room layout but are optional: - patient/staff call (although required when for patient use); The following items may be provided: - a tip-up seat
| ADB | [7 empty] | Room Environmental Data
V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL006 |  | PULL CORD, patient/staff call (help) with reassurance lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SEA004 |  | SEAT, bench, wall mounted, 480H 1300W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0725-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0725-01 |  |  |  |  | Changing room: semi-ambulant: pass-through
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Semi-ambulant person may undress/dress in privacy. 2) Hanging outdoor clothing. 3) Call systems may be used.
| Personnel: | [6 empty] | 1 x person. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2.5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room.
| ADB | [7 empty] | Room Environmental Data
V0725-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0725-01 |  |  |  |  | Changing room: semi-ambulant: pass-through
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0725-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0725-01 |  |  |  |  | Changing room: semi-ambulant: pass-through
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0725-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0725-01 |  |  |  |  | Changing room: semi-ambulant: pass-through
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL006 |  | PULL CORD, patient/staff call (help) with reassurance lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI081 |  | RAIL, grab, horizontal, wall mounted, 900mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SEA004 |  | SEAT, bench, wall mounted, 480H 1300W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0726
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0726 |  |  |  |  | Changing room: independent wheelchair
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Wheelchair user may undress/dress independently in privacy. 2) Hanging clothing whilst seated. 3) Call systems may be used.
| Personnel: | [6 empty] | 1 x person. Intermittent use.
| Planning Relationships: | [5 empty] | Adjacent to sub-waiting area (if provided). Close to WC facilities.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 4.5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items may be provided: - a bench (instead of the tip-up seat shown on the room layout).
| ADB | [7 empty] | Room Environmental Data
V0726
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0726 |  |  |  |  | Changing room: independent wheelchair
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0726
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0726 |  |  |  |  | Changing room: independent wheelchair
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0726
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0726 |  |  |  |  | Changing room: independent wheelchair
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL006 |  | PULL CORD, patient/staff call (help) with reassurance lamp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | RAI161 |  | RAIL, grab, horizontal, wall or door mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI172 |  | RAIL, grab, hinged, wall mounted, 650mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SEA022 |  | SEAT, tip-up, fixed height | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0726-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0726-01 |  |  |  |  | Changing room: independent wheelchair: pass-through
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Wheelchair user may undress/dress independently in privacy. 2) Hanging clothing whilst seated. 3) Call systems may be used. 4) Semi-ambulant person may undress/dress in privacy.
| Personnel: | [6 empty] | 1 x person. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items may be provided: - a bench (instead of the tip-up seat shown on the room layout).
| ADB | [7 empty] | Room Environmental Data
V0726-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0726-01 |  |  |  |  | Changing room: independent wheelchair: pass-through
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0726-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0726-01 |  |  |  |  | Changing room: independent wheelchair: pass-through
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0726-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0726-01 |  |  |  |  | Changing room: independent wheelchair: pass-through
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL006 |  | PULL CORD, patient/staff call (help) with reassurance lamp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | RAI161 |  | RAIL, grab, horizontal, wall or door mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI172 |  | RAIL, grab, hinged, wall mounted, 650mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SEA022 |  | SEAT, tip-up, fixed height | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0922
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0922 |  |  |  |  | WC: independent wheelchair
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Independent wheelchair accessible toilet and adjacent hand-rinse basin may be used. 2) Call systems may be used.
| Personnel: | [6 empty] | 1 x person. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 4.5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items are shown on the drawing but are optional: - the bin for the disposal of sanitary towels is only required in female WCs;
| ADB | [7 empty] | Room Environmental Data
V0922
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0922 |  |  |  |  | WC: independent wheelchair
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 20
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0922
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0922 |  |  |  |  | WC: independent wheelchair
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0922
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V0922 |  |  |  |  | WC: independent wheelchair
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAC002 |  | BACKREST, WC/toilet, padded, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL006 |  | PULL CORD, patient/staff call (help) with reassurance lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CIS005 |  | CISTERN WC/toilet, concealed, reversible. To suit WC | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | RAI048 |  | RAIL, grab, vertical, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI159 |  | RAIL, grab, horizontal, with supports, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI161 |  | RAIL, grab, horizontal, wall or door mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI172 |  | RAIL, grab, hinged, wall mounted, 650mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WCH005 |  | WC/toilet pan with seat, 700 mm projection, hospital pattern, rimless pan, vitreous china. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS015 |  | DISPENSER, toilet paper, dispense individual sheets, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE100 |  | SHELF, raised edge, non-breakable, 600W 200D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE102 |  | SHELF, raised edge, non-breakable, 200W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | VEN003 |  | VENDING MACHINE, sanitary towel with coin slot | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN028 |  | BIN, disposal, sealed, operated with one hand, nominal 420H 155W 490D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL003 |  | HOLDER, sack, small, freestanding | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Toilet may be used by ambulant person. 2) Hand-rinse basin may be used.
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following items are shown on the drawing but are optional: - the bin for the disposal of sanitary towels is only required in female WCs; - the shelf next to the basin.
| ADB | [7 empty] | Room Environmental Data
V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 20
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CIS005 |  | CISTERN WC/toilet, concealed, reversible. To suit WC | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WCH001 |  | WC/toilet pan with seat, 520-550 projection, hospital pattern, rimless pan, vitreous china. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL016 |  | HOLDER, toilet roll, multi, large | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN028 |  | BIN, disposal, sealed, operated with one hand, nominal 420H 155W 490D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL004 |  | HOLDER, sack, with lid foot operated, small, freestanding | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V1121
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1121 |  |  |  |  | WC: semi-ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Toilet may be used by semi-ambulant person. 2) Hand-rinse basin may be used. 3) Call systems may be used.
| Personnel: | [6 empty] | 1 x person. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2.5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items are shown on the drawing but are optional: - the bin for the disposal of sanitary towels is only required in female WCs; - the shelf next to the basin. The following items may be provided: - mirror.
| ADB | [7 empty] | Room Environmental Data
V1121
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1121 |  |  |  |  | WC: semi-ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 20
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V1121
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1121 |  |  |  |  | WC: semi-ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V1121
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1121 |  |  |  |  | WC: semi-ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL006 |  | PULL CORD, patient/staff call (help) with reassurance lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CIS005 |  | CISTERN WC/toilet, concealed, reversible. To suit WC | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR001 |  | MIRROR, wall mounted, 650H 300W | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | RAI048 |  | RAIL, grab, vertical, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI158 |  | RAIL, grab, horizontal, wall / door mounted, 500mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI161 |  | RAIL, grab, horizontal, wall or door mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI172 |  | RAIL, grab, hinged, wall mounted, 650mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WCH001 |  | WC/toilet pan with seat, 520-550 projection, hospital pattern, rimless pan, vitreous china. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS015 |  | DISPENSER, toilet paper, dispense individual sheets, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN028 |  | BIN, disposal, sealed, operated with one hand, nominal 420H 155W 490D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL004 |  | HOLDER, sack, with lid foot operated, small, freestanding | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V1131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1131 |  |  |  |  | Nappy changing room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Changing nappies. 2) Clinical waste may be disposed 3) Wash-hand basin may be used.
| Personnel: | [6 empty] | 1 x baby or infant. 1 x adult (ambulant).
| Planning Relationships: | [5 empty] | Adjacent to waiting area and/or concourse
| Space Data: | [6 empty] | Area (m²): |  |  |  | 5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The room includes a wall-mounted fold-down changing table, alternatively, it can accommodate a fixed or mobile table. The layout is suitable for ambulant and semi-ambulant users, where access is required for wheelchair users, consideration must be given to the space within the room and fixing height of the changing table.
| ADB | [7 empty] | Room Environmental Data
V1131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1131 |  |  |  |  | Nappy changing room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V1131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1131 |  |  |  |  | Nappy changing room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V1131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1131 |  |  |  |  | Nappy changing room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS107 |  | BASIN, medium, general pattern, vitreous china, 2 tap holes, no overflow, bottom outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | NCU001 |  | BABY NAPPY CHANGING UNIT, folds up base, heavy duty plastic, safety straps, wall mounted, 900H 560W 885D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA383 |  | CHAIR, stacking, polypropylene, with back and seat pads, wipeable. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL008 |  | HOLDER, sack with lid foot operated, large, freestanding, 960H 500W 415D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Shower may be used by ambulant person. 2) User may undress and dress in privacy. 3) Hanging outdoor clothing. 4) Hanging clothes and towels.
| Personnel: | [6 empty] | 1 x person (staff or visitor). Intermittent use.
| Planning Relationships: | [5 empty] | Associated with staff changing area. Close to a WC.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2.5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | This room is not recommended for patient use. The following items may be provided: - inward opening door; - full length mirror.
| ADB | [7 empty] | Room Environmental Data
V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 100-150
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | DIS200 |  | DISH, soap, wall mounted | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG063 |  | LUMINAIRE, single fluorescent lamp, wall, 8 watt, 300 mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR002 |  | MIRROR, wall mounted, 900H 300W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT025 |  | SOCKET outlet, shaver | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI260 |  | RAIL for shower curtain, 1000mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SEA024 |  | SEAT, tip-up, wall mounted, 400 W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO009 |  | SHOWER TRAY ceramic slip resistant base, with drainage outlet, 800W 800D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO018 |  | SHOWER, valve, thermostatic mixer (associated with SHO020). | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO020 |  | SHOWER, adjustable shower head hand spray (associated with SHO018). | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC014 |  | SWITCH 5amp ac single pole, 1 way, ceiling pull cord | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V1323
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1323 |  |  |  |  | Shower room: semi-ambulant: standing use
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Shower may be used by semi-ambulant person (whilst standing). 2) Toilet may be used by semi-ambulant person. 3) Wash-hand basin may be used. 4) User may undress and dress in privacy. 5) Hanging outdoor clothing. 6) Hanging clothes and towels. 7) Call systems may be used.
| Personnel: | [6 empty] | 1 x person. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items are shown on the drawing but are optional: - the bin for the disposal of sanitary towels is only required in female WCs; - mirror, light and shaver outlet. The following items may be provided: - modular shelf.
| ADB | [7 empty] | Room Environmental Data
V1323
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1323 |  |  |  |  | Shower room: semi-ambulant: standing use
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V1323
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1323 |  |  |  |  | Shower room: semi-ambulant: standing use
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V1323
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1323 |  |  |  |  | Shower room: semi-ambulant: standing use
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS107 |  | BASIN, medium, general pattern, vitreous china, 2 tap holes, no overflow, bottom outlet, 500W 400D. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | CAL006 |  | PULL CORD, patient/staff call (help) with reassurance lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CIS005 |  | CISTERN WC/toilet, concealed, reversible. To suit WC | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS200 |  | DISH, soap, wall mounted | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG063 |  | LUMINAIRE, single fluorescent lamp, wall, 8 watt, 300 mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR002 |  | MIRROR, wall mounted, 900H 300W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT025 |  | SOCKET outlet, shaver | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT345 |  | OUTLET, floor drainage and grating, 150 mm dia. hospital pattern. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | RAI048 |  | RAIL, grab, vertical, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI078 |  | RAIL, grab, horizontal, cranked, U-shape, wall mounted, 1200W 900D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI158 |  | RAIL, grab, horizontal, wall / door mounted, 500mm | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | RAI161 |  | RAIL, grab, horizontal, wall or door mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI172 |  | RAIL, grab, hinged, wall mounted, 650mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI262 |  | RAIL for shower curtain, 1200mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SEA024 |  | SEAT, tip-up, wall mounted, 400 W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO005 |  | SHOWER, slip resistant floor, with drainage outlet, 1200W 1200D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO018 |  | SHOWER, valve, thermostatic mixer (associated with SHO020). | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO020 |  | SHOWER, adjustable shower head hand spray (associated with SHO018). | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC014 |  | SWITCH 5amp ac single pole, 1 way, ceiling pull cord | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP347 |  | TAP, pillar, short lever, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WCH001 |  | WC/toilet pan with seat, 520-550 projection, hospital pattern, rimless pan, vitreous china. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS015 |  | DISPENSER, toilet paper, dispense individual sheets, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN028 |  | BIN, disposal, sealed, operated with one hand, nominal 420H 155W 490D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V1906
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1906 |  |  |  |  | WC, wash: wheelchair accessible, radiation protective
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Using WC. 2) Using washbasin. 3) Hanging outdoor clothing. 4) Call systems may be used.
| Personnel: | [6 empty] | 1 x Person Intermittent use
| Planning Relationships: | [5 empty] | Adjacent to Gamma Camera Room Adjacent to "Hot" waiting room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 4.5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Discharge must be direct to main sewer. WC water trap to be marked with radiation symbol. Sanitary towel disposal facilities if required as local policy. Sign indicating: "WC for use by Radio-isotope Patients only".
| ADB | [7 empty] | Room Environmental Data
V1906
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1906 |  |  |  |  | WC, wash: wheelchair accessible, radiation protective
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V1906
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1906 |  |  |  |  | WC, wash: wheelchair accessible, radiation protective
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - radiation protection: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V1906
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | V1906 |  |  |  |  | WC, wash: wheelchair accessible, radiation protective
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL002 |  | PUSH BUTTON patient/staff call, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL009 |  | PULL CORD, staff emergency call with indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL029 |  | LAMP patient reassurance, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CIS005 |  | CISTERN WC/toilet, concealed, reversible. To suit WC | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR001 |  | MIRROR, wall mounted, 650H 300W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI048 |  | RAIL, grab, vertical, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI056 |  | RAIL, towel, single, stainless steel, 15mm dia. 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI065 |  | RAIL, grab, horizontal, cranked, L-shape, wall mounted, 1100W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI079 |  | RAIL, grab, horizontal, wall mounted, 750mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI161 |  | RAIL, grab, horizontal, wall or door mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI175 |  | RAIL, grab, hinged, wall mounted, 750mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | STF200 |  | STORAGE UNIT, mid, shelf, 150H 300W 150D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WCH005 |  | WC/toilet pan with seat, 700 mm projection, hospital pattern, rimless pan, vitreous china. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL018 |  | HOLDER, toilet roll | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL003 |  | HOLDER, sack, small, freestanding | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W0540
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W0540 |  |  |  |  | Store: clinical/sterile supplies
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Sterile equipment, consumable supplies and packs are stored.
| Personnel: | [6 empty] | 1 x Staff Intermittent use
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
Notes:
| ADB | [7 empty] | Room Environmental Data
W0540
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W0540 |  |  |  |  | Store: clinical/sterile supplies
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 16 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | +ve & -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W0540
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W0540 |  |  |  |  | Store: clinical/sterile supplies
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W0540
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W0540 |  |  |  |  | Store: clinical/sterile supplies
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SHE222 |  | SHELF, 1200W 400D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC051 |  | CABINET, tall, modular storage, for 600 facing inserts, open, on plinth, 2100H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMF011 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 465D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SMF013 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 665D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | STO008 |  | STOOL, kick, retractable castors | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W1584-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1584-01 |  |  |  |  | Store: clinical equipment
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Medical equipment is stored. 2) Large items of equipment are stored. 3) Mobile equipment may be parked and stored and/or recharged. 4) Equipment is placed on charge.
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | This store includes a mixture of shelving and racking for small equipment and floor space for large equipment.
| ADB | [7 empty] | Room Environmental Data
W1584-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1584-01 |  |  |  |  | Store: clinical equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200/300 |  | Subject to perception of detail required
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W1584-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1584-01 |  |  |  |  | Store: clinical equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W1584-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1584-01 |  |  |  |  | Store: clinical equipment
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 14 |  |  | 14 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PEG005 |  | PEGS, equipment, 3 (500mm spacing), wall mounted | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SHE253 |  | SHELF, 2100W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLI017 |  | CLIP, spring, 32mm dia. 3, mounted on a wooden batten, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SMF011 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 465D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | STO008 |  | STOOL, kick, retractable castors | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W1584-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1584-02 |  |  |  |  | Store: clinical equipment
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Medical equipment is stored. 2) Large items of equipment are stored. 3) Mobile equipment may be parked and stored and/or recharged. 4) Equipment is placed on charge.
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | This store includes a mixture of shelving and racking for small equipment and floor space for large equipment..
| ADB | [7 empty] | Room Environmental Data
W1584-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1584-02 |  |  |  |  | Store: clinical equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200/300 |  | Subject to perception of detail required
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W1584-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1584-02 |  |  |  |  | Store: clinical equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W1584-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1584-02 |  |  |  |  | Store: clinical equipment
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 9 |  |  | 9 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PEG005 |  | PEGS, equipment, 3 (500mm spacing), wall mounted | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SHE253 |  | SHELF, 2100W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CLI017 |  | CLIP, spring, 32mm dia. 3, mounted on a wooden batten, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SMF011 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 465D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | STO008 |  | STOOL, kick, retractable castors | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W1585-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1585-01 |  |  |  |  | Store: general
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Miscellaneous equipment is stored. 2) Non-clinical supplies are stored.
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 4 |  |  |  |  | Height (mm): |  |  |  | 2400
Notes:
| ADB | [7 empty] | Room Environmental Data
W1585-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1585-01 |  |  |  |  | Store: general
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200/300 |  | Subject to perception of detail required
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W1585-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1585-01 |  |  |  |  | Store: general
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W1585-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1585-01 |  |  |  |  | Store: general
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | SHE211 |  | SHELF, 900W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMF011 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 465D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W1585-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1585-02 |  |  |  |  | Store: general
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Miscellaneous equipment is stored. 2) Non-clinical supplies are stored.
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
Notes:
| ADB | [7 empty] | Room Environmental Data
W1585-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1585-02 |  |  |  |  | Store: general
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200/300 |  | Subject to perception of detail required
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W1585-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1585-02 |  |  |  |  | Store: general
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W1585-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1585-02 |  |  |  |  | Store: general
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 15 |  |  | 15 |  |  |  |  | SHE211 |  | SHELF, 900W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMF011 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 465D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W1594
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1594 |  |  |  |  | Store: linen
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Linen and/or towels are stored. 2) Bedding, blankets and pillows are stored. 3) Holding distribution trolley. 4) Holding exchange trolley.
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Close to treatment/diagnostic rooms.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 6 |  |  |  |  | Height (mm): |  |  |  | 2400
Notes:
| ADB | [7 empty] | Room Environmental Data
W1594
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1594 |  |  |  |  | Store: linen
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W1594
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1594 |  |  |  |  | Store: linen
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W1594
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | W1594 |  |  |  |  | Store: linen
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRO231 |  | TROLLEY, clean linen distribution, 4 containers, 2 door, 1495H 1350W 590D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO233 |  | TROLLEY, clean linen exchange, 3 adjustable shelves, large, 1600H 1600W 680D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | X0231
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | X0231 |  |  |  |  | Resuscitation bay: 1 place
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Resuscitation procedures. 2) Oxygen and vacuum services may be used for resuscitation. 3) Controlled and scheduled drugs are stored securely. 4) Clinical hand washing. 5) Statutory notices. may be displayed
| Personnel: | [6 empty] | 1 x Patient 5 x Staff
| Planning Relationships: | [5 empty] | Convenient to MRI Scanner Room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 10 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Lamp indicator call situated over door outside room. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
X0231
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | X0231 |  |  |  |  | Resuscitation bay: 1 place
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -Ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Anaesthetic gases in use. Provide clean air flow path
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 1000
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | X0231
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | X0231 |  |  |  |  | Resuscitation bay: 1 place
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | X0231
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | X0231 |  |  |  |  | Resuscitation bay: 1 place
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP290 |  | CUPBOARD, 4 shelves, lockable, wall mounted, 550H 650W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG053 |  | LUMINAIRE, examination, ceiling, adjustable, 1000 lux | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG081 |  | LUMINAIRE fitted with single fluorescent lamp with switch, below drug cupboard, 8watt, 400mm | [16 empty] | 1
| 17 |  |  | 17 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT050 |  | OUTLET, controlled drugs cupboard | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT056 |  | CONNECTION UNIT, unswitched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT461 |  | OUTLET, nitrous oxide, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT480 |  | OUTLET, gas scavenging (AGS), medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | STF127 |  | STORAGE UNIT, lower, cupboard, 2 door, 1 shelf, 550H 600W 450D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | STF164 |  | STORAGE UNIT, lower, 6 drawer, 550H 600W 450D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | STF290 |  | STORAGE UNIT, upper, cupboard, controlled drugs, 1 door, lockable, with warning light, 550H 600W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SUC002 |  | SUCTION UNIT, pipeline, high pressure, theatre | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRA103 |  | TRACK, curtain, one sided, 1600mm length | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WKT150 |  | WORKTOP, cantilevered from wall, 2100W 650D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS010 |  | DISPENSER, pack, wall mounted, 600H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | X0231
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | X0231 |  |  |  |  | Resuscitation bay: 1 place
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | TRO130 |  | TROLLEY, dressing/instrument, stainless steel, antistatic castors, 870H 450W450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO310 |  | TROLLEY, emergency/resuscitation, complete with defibrillator, 955H 825W 575D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | X1025
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | X1025 |  |  |  |  | Neuroangiography room: biplane No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may arrive on a trolley. 2) Patient is transferred to the imaging table. 3) Neuroangiography investigation - patient to undergo Angiography examination. 4) Viewing, retrieving and archiving x-ray films/images. 5) General or local anaesthetic or sedation may be administered. 6) Physiological monitoring equipment may be used. 7) Contrast media may be administered. 8) Disposal of waste.
| Personnel: | [6 empty] | 1 x Patient 10 x Staff
| Planning Relationships: | [5 empty] | Close to neurosurgical operating theatre. Close to critical care units (CCU). Close to A&E.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 55 |  |  |  |  | Height (mm): |  |  |  | 2950
| Notes: | [7 empty] | Radiation protection as required. Lighting control panel giving variable levels of illumination.
| ADB | [7 empty] | Room Environmental Data
X1025
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | X1025 |  |  |  |  | Neuroangiography room: biplane No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 22
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Anaesthetic gases in use. Provide clean air flow path
LIGHTING
Type Of Control:
Daytime General Service Illuminance (Lux):
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | N
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | X1025
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | X1025 |  |  |  |  | Neuroangiography room: biplane No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset- radiation protection: 1 x personnel, bed, trolley, wheelchair & equipment access (1900mm); Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Essential Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | X1025
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | X1025 |  |  |  |  | Neuroangiography room: biplane No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG050 |  | LUMINAIRE operating (minor) | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG081 |  | LUMINAIRE fitted with single fluorescent lamp with switch, below drug cupboard, 8watt, 400mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC001 |  | CABINET tall, 600mm facing, (600x400 inserts), with formed plastic liners, open, on plinth, o/a height 2100 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC002 |  | CABINET tall, 600mm facing, (600x400 inserts), with formed plastic liners and 10 telescopic runners, open, on plinth, o/a height 2100 | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | MSC187 |  | CABINET base, 400mm facing, with 2 shelves, 1 door hinged right, on plinth, o/a height 900 | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | MSC188 |  | CABINET base, 400mm facing, with 2 shelves, 1 door hinged left, on plinth, o/a height 900 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | MSC192 |  | CABINET top, 400mm facing, with 1 shelf, 1 door hinged right, wall mounted | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | MSC193 |  | CABINET top, 400mm facing, with 1 shelf, 1 door hinged left, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MSC520 |  | CATHETER CUPBOARD, 600mm facing, with formed plastic liners, incl. shelf with 5 telescopic rails, open, on plinth, o/a height 2100 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | MSW015 |  | WORKTOP, for 5x 400mm facing inserts cabinets, 2275W 700D nominal | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT050 |  | OUTLET, controlled drugs cupboard | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT056 |  | CONNECTION UNIT, unswitched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PEN001 |  | PENDANT medical supply unit outlets: 2x 13amp switched double, Medical Oxygen, Medical Nitrous Oxide, Vacuum medical, MA4, AGS | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PEN002 |  | PENDANT ANAESTHETIC medical and power supply unit, vertical movement, ceiling mounted, outlets comprising: 4x socket outlet, 13amp, switched, double 1x outlet oxygen, medical 1x outlet nitrous oxide, medical 1x outlet compressed air medical, (4 bar) 1x outlet compressed air surgical, (7 bar) 2x outlet vacuum, medical 1x AGS, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | STF128 |  | STORAGE UNIT, lower, cupboard, 2 door, 1 shelf, lockable, 550H 600W 450D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | STF162 |  | STORAGE UNIT, lower, 4 drawer, 550H 600W 450D | [16 empty] | 1
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | X1025
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | X1025 |  |  |  |  | Neuroangiography room: biplane No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | STF181 |  | STORAGE UNIT, lower, open shelf carcase, 2 shelves, 550H 600W 450D | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | STF275 |  | STORAGE UNIT, upper, cupboard, 2 door, 1 shelf, lockable, 550H 600W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | STF286 |  | STORAGE UNIT, upper, cupboard, medicine, 2 door, lockable, 550H 600W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | STF290 |  | STORAGE UNIT, upper, cupboard, controlled drugs, 1 door, lockable, with warning light, 550H 600W 300D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP815 |  | *TAP bib combination assembly 2x12mm, mixer, double lever action, fixed nozzle, HTM64TBH3. Replaced by: TAP 894, 15/05/06 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRO602 |  | TROUGH scrub-up, hospital pattern, stainless steel, double, 75mm upstand, 950H 1600W 450D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WKT152 |  | WORKTOP, cantilevered from wall, 2400W 650D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB034 |  | CABINET warming, contrast media, stainless steel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CRD053 |  | CONTROL CONSOLE - physiologic monitoring system, cardiac catheterization | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS006 |  | DISPENSER, disposable nailbrush, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF091 |  | REFRIGERATOR, drug, capacity 35 litre, external temperature gauge, lockable, wall mounted, 510H 380W 445D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | ANA004 |  | ANAESTHETIC MACHINE/WORKSTATION with ventilator, with accessories, mobile, 1580H 565W 695D | [16 empty] | 3
| 5 |  |  | 5 |  |  |  |  | IMG101 |  | MONITOR viewing, flat panel display for image intensifier, ceiling mounted | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MST001 |  | TROLLEY, single open frame, with handle, up to 5 sets of runners, 600mm facing, approx 850H 730W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STA142 |  | STAND, infusion, twin hook, breaks, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SYR001 |  | SYRINGE INJECTOR, automatic, hi pressure injection, contrast media | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO133 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 750W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO310 |  | TROLLEY, emergency/resuscitation, complete with defibrillator, 955H 825W 575D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | X1026
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | X1026 |  |  |  |  | Control room: serving neuroangiography No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Using the operating console to control each scan and monitor the VDT image. 2) Retrieving and archiving stored data. 3) Producing hard copy of selected images. 4) Communication with colleagues/offices/departments may occur by telephone. 5) Reference books and notices are studied. 6) Small items of equipment are held stored 7) Stationery/paper is stored. 8) Writing notes.
| Personnel: | [6 empty] | Up to 3 Staff
| Planning Relationships: | [5 empty] | En-suite to laboratory room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 16 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Good visual & voice contact with the laboratory. Radiation protection as required. Activity note: Receiving colleagues/visitors for training/observation of angiography session.
| ADB | [7 empty] | Room Environmental Data
X1026
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | X1026 |  |  |  |  | Control room: serving neuroangiography No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 22
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
Type Of Control:
Daytime General Service Illuminance (Lux):
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | N
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | X1026
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | X1026 |  |  |  |  | Control room: serving neuroangiography No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors - radiation protection: 2 x personnel access (900mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Essential Radiation proof glazing to control room Roller blind on cath. lab. room side Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | X1026
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | X1026 |  |  |  |  | Control room: serving neuroangiography No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT133 |  | SOCKET outlet, computer data, double | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT207 |  | SOCKET outlet aerial television, closed circuit (CCTV) | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SMC016 |  | CABINET, base, modular storage, for 400 facing inserts, 4 drawers, on plinth, 900H | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SMC017 |  | CABINET, base, modular storage, for 400 facing inserts, 3 drawers, on plinth, 900H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMW054 |  | WORKTOP, clinical, for 4 x 400 facing modular storage cabinets, 1820W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CRD051 |  | CONTROL CONSOLE and COMPUTER for catheter laboratories, (Part of CRD021 or CRD023) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG111 |  | CONTROL CONSOLE - tableside gantry control for digital imaging system | [16 empty] | 2
| 3 |  |  | 3 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0331
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0331 |  |  |  |  | Dirty utility room: bedpan processing
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Disposal of liquid waste. 2) Disposal of bedpans, urine bottles and vomit bowls with contents. 3) Cleansing bedpan holders. 4) Holding/storing working supplies of disposable bedpans, urine bottles and vomit bowls. 5) Holding SHARPS in a container. 6) Items requiring disposal or reprocessing may be held/stored. 7) Holding dirty linen. 8) Sani-chairs and commodes may be parked and/or stored. 9) Clinical wash-hand basin may be used. 10) Urine specimens may be tested. 11) Clinical waste may be disposed 12) Disposal of waste and contaminated materials. 13) Disposal of used protective clothing. 14) Disposal of non-clinical waste.
| Personnel: | [6 empty] | 2 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Close to clinical area, particularly treatment rooms.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The following items may be provided: - placenta weighing scales.
| ADB | [7 empty] | Room Environmental Data
Y0331
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0331 |  |  |  |  | Dirty utility room: bedpan processing
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0331
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0331 |  |  |  |  | Dirty utility room: bedpan processing
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0331
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0331 |  |  |  |  | Dirty utility room: bedpan processing
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU001 |  | DISPOSAL UNIT (macerator), disposable bedpan, bedpan liners/urine bottles, 525W 650D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU006 |  | DISPOSAL UNIT, plain top, right hand drainer, with sink and hopper with flushing rim, 110mm outlet, no tap holes no overflow, back inlet, stainless steel, 1600W 600D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT079 |  | OUTLET isolator, equipment manufacturer's specification | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT301 |  | OUTLET, cold water for equipment | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC023 |  | CABINET, upper, modular storage, for 400 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW052 |  | WORKTOP, clinical, for 2 x 400 facing modular storage cabinets, 910W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS004 |  | DISPENSER, disposable bedpans, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS005 |  | DISPENSER, disposable urine bottles, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS007 |  | DISPENSER, paper towel roll, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS442 |  | DISPENSER, vomit bowls, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | RAC001 |  | RACK, drainage, bedpan holder (5), with drip tray, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CHA338 |  | SANI-CHAIR/COMMODE, tubular, metal, wipeable, mobile. | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0431
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0431 |  |  |  |  | Dirty utility room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Disposal of liquid waste. 2) Holding SHARPS in a container. 3) Items requiring disposal or reprocessing may be held/stored. 4) Clinical wash-hand basin may be used. 5) Urine specimens may be tested. 6) Clinical waste may be disposed 7) Disposal of waste and contaminated materials. 8) Disposal of used protective clothing. 9) Disposal of non-clinical waste.
| Personnel: | [6 empty] | 2 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Close to clinical area, particularly treatment rooms.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
Y0431
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0431 |  |  |  |  | Dirty utility room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0431
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0431 |  |  |  |  | Dirty utility room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0431
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0431 |  |  |  |  | Dirty utility room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU006 |  | DISPOSAL UNIT, plain top, right hand drainer, with sink and hopper with flushing rim, 110mm outlet, no tap holes no overflow, back inlet, stainless steel, 1600W 600D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC023 |  | CABINET, upper, modular storage, for 400 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW052 |  | WORKTOP, clinical, for 2 x 400 facing modular storage cabinets, 910W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS007 |  | DISPENSER, paper towel roll, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 4 |  |  | 4 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0642
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0642 |  |  |  |  | Disposal hold: 1700 litres
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Holding domestic, clinical and recyclable waste for disposal or reprocessing
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Adjacent to main circulation route.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2700
Ceiling height must allow bin lids to open fully.
| Notes: | [7 empty] | Separate bins/areas must be provided for: - clinical waste; - domestic waste; - recyclable items; - linen; - equipment requiring reprocessing.
| ADB | [7 empty] | Room Environmental Data
Y0642
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0642 |  |  |  |  | Disposal hold: 1700 litres
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0642
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0642 |  |  |  |  | Disposal hold: 1700 litres
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley, & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0642
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0642 |  |  |  |  | Disposal hold: 1700 litres
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BIN034 |  | BIN wheelie, 240 litre, 1060H 600W 730D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | BIN038 |  | BIN wheelie, 1100 litre, 1470H1370W 1115D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0646
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0646 |  |  |  |  | Disposal hold: 3000 litres
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Holding domestic, clinical and recyclable waste for disposal or reprocessing
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Adjacent to main circulation route.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
Ceiling height must allow bin lids to open fully.
| Notes: | [7 empty] | Separate bins/areas must be provided for: - clinical waste; - domestic waste; - recyclable items; - linen; - equipment requiring reprocessing.
| ADB | [7 empty] | Room Environmental Data
Y0646
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0646 |  |  |  |  | Disposal hold: 3000 litres
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0646
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0646 |  |  |  |  | Disposal hold: 3000 litres
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0646
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0646 |  |  |  |  | Disposal hold: 3000 litres
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BIN037 |  | BIN wheelie, 770 litre, 1360H1360W 800D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0661
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0661 |  |  |  |  | Disposal hold: radioactive waste
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Holding radioactive waste for collection/disposal.
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Away from working areas/public areas. Direct access from outside and inside of the building, for out of hours delivery and collection.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 3 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | Refer to code of practice for the Protection of Persons against Ionising Radiations arising from Medical and Dental use for special requirements precautions. Refer to Building Note regarding use of this room. Number and type of cabinets to suit various levels of radioactive waste stored The following items may be provided: - Room may require security access (eg. digital or electronic lock), plus radiation warning sign on the door.
| ADB | [7 empty] | Room Environmental Data
Y0661
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0661 |  |  |  |  | Disposal hold: radioactive waste
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
Type Of Control:
Daytime General Service Illuminance (Lux):
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | N
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0661
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0661 |  |  |  |  | Disposal hold: radioactive waste
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0661
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y0661 |  |  |  |  | Disposal hold: radioactive waste
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CAB171 |  | CABINET: radioactive material decay | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Disposal of liquid waste. 2) Filling and emptying cleaning equipment and containers. 3) Holding/storing cleaning equipment. 4) Cleaning equipment may be parked and/or stored. 5) Hand-rinse basin may be used. 6) Sink may be used. 7) Janitorial unit may be used.
| Personnel: | [6 empty] | 2 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Close to areas served.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
If large equipment is stored elsewhere, the size of this room can be reduced.
| Notes: | [7 empty] | This room represents a typical traditional cleaners' room with space for storing a vacuum cleaner, scrubbing/polishing machine (for hard floors) and mop and bucket (stored on the cleaners' trolley). It includes a combined bucket sink and hand-rinse basin (janitorial unit) and separate sink. The following items are shown on the room layout but are optional: - small cube lockers.
| ADB | [7 empty] | Room Environmental Data
Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 22
| Unified Glare Rating Limit (UGRL): | [13 empty] | 80
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Heat
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN06 |  |  |  |  | Facilities for diagnostic imaging and interventional radiology V1 and V2 - list of spaces
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | HOO020 |  | HOOK, single, large, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE231 |  | SHELF, 1500W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SIN013 |  | SINK and BASIN combination Janitorial unit, hinged bucket grating to sink and monobloc mixer tap with swivel nozzle, stainless steel, 900H 500W 600D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SNU012 |  | SINK UNIT, single bowl with right hand drainer, no tap holes, 1200W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLI017 |  | CLIP, spring, 32mm dia. 3, mounted on a wooden batten, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | LOC012 |  | LOCKER, wall mounted, 340H 300W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLE008 |  | SCRUBBING/POLISHING MACHINE, single brush, 110v machine | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CLE018 |  | CLEANER VACUUM, dry suction, tub, with accessories, filtered air exhaust | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | CON061 |  | CONE, warning, 'wet floor' | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL014 |  | HOLDER, sack, with lid foot operated, large, capacity 120 litre, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAD002 |  | LADDER, 3 tread, platform type 750mm height, folding | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO068 |  | TROLLEY, cleaners, mop bucket, 3 shelves tray and waste sack holder, 980H 1170W 550D | [16 empty] | 3
Activity DataBase
2016-12-28