## Sheet1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | B2425
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | B2425 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Post anaesthetic recovery of patients. 2) Medical and nursing procedures. 3) Observation is undertaken by medical and nursing staff. 4) Clinical wash-hand basin may be used. 5) Mobile equipment and services may be used. 6) Moving/ Manoeuvring beds. 7) Monitoring/diagnostic or therapeutic equipment may be used. 8) Piped medical gases, vacuum and associated equipment may be used.
| Personnel: | [6 empty] | 1 x patient. 1 x staff. 1 x other.
| Planning Relationships: | [5 empty] | Part of multi-bay area. Overall area to include staff communication base and utilities. Close to operating theatre.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 14 |  |  |  |  | Height (mm): |  |  |  | 2700
2700 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | The call repeat lamp is situated outside of the bay. A staff emergency call linked to an emergency call repeat lamp in the staff communications base and each operating theatre required. Note the engineering services included in this data sheet comply with the requirements of HTM 08-03 and superseded the text in para 4.154 of HBN 26-1 and 3.175 of HBN 10-02. For dedicated maternity recovery may only include 1 no. of each s outlet. The following items are shown on the room layout but are optional: - cleaning socket outlet may be shared between multiple bays (9m max cable); - light switch for multiple bay space. The following items may be provided: - when used for maternity provision of a cot(s) may be required; - ceiling-mounted hoist, subject to local policy; - lead protection for mobile imaging, subject to RPA advice. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
B2425
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | B2425 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 500 |  | WP
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
| Standby Lighting Grade - Local Lighting: | [13 empty] | A
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45 |  | The LAmax,f dB noise limit applies only at night 23:00 to 07:00 hours.
| Noise Intrusion (dB) 1hr night: | [13 empty] | 35
| Noise Intrusion (dB) f night: | [13 empty] | 45
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | B2425
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | B2425 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England. All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | B2425
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | B2425 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL035 |  | LAMP repeat call (patient/staff or staff emergency or Cardiac call), ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | IMG002 |  | MONITOR medical display 18"; digital image viewer, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG058 |  | LUMINAIRE, examination, wall, adjustable, 1000 lux | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | RAI130 |  | RAIL, clinical equipment, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRA106 |  | TRACK, curtain, one sided, 4000mm length | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BRA015 |  | BRACKET, flat panel monitor, height adjustable, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL020 |  | HOLDER, sharps box, up to 7 litre capacity, rail/trolley hang or wall mounted, 170H 125W 100D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT002 |  | TROLLEY, modular storage, single open frame, including handle and worktop, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STO006 |  | STOOL, surgeon/anaesthetist, height adjustable, includes anti-static seat pads | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | C0237
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | C0237 |  |  |  |  | Consulting/examination room: double-sided couch access
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Consultations may take place. 2) Sterile supplies and consumables are stored on a trolley. 3) User may undress and dress in privacy. 4) Electronic patient records (EPRs) may be accessed and updated. 5) Clinical hand washing. 6) Discussions and interviews may take place. 7) Carrying out examinations and assessment of patient. 8) Patient may arrive on foot or in a wheelchair. 9) Examinations of the patient may be carried out from one or both sides of the couch. 10) Minimally invasive clinical procedures may be undertaken from one or both sides of the couch. 11) Call systems may be used.
| Personnel: | [6 empty] | 1 x patient. 1-2 x staff. 1 x other (escort).
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 16 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | This room includes a 3-section couch, alternatively, it may accommodate a 2-section couch or specialist couch. The call repeat lamp is situated over the door outside the room. The following items are shown on the room layout but are optional: - patient/staff call (although expected where a patient will be left unattended); - room in use switch and indicator. The following items may be provided: - a small printer; - a small lockable drawer; - dimming switch. Piped medical gases may be required for some clinical specialties. Workstations have been placed in Consult/ exam rooms at 900mmm. Local policy may prefer a desk up to 1200mm to facilitate working practice. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
C0237
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | C0237 |  |  |  |  | Consulting/examination room: double-sided couch access
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | WP
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 1000 |  | Bed level (provided by the mobile examinantion lamp)
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | C0237
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | C0237 |  |  |  |  | Consulting/examination room: double-sided couch access
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | C0237
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | C0237 |  |  |  |  | Consulting/examination room: double-sided couch access
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL003 |  | PUSH BUTTON, patient/staff call (help) with socket for patient hand-held unit | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG053 |  | LUMINAIRE, examination, ceiling, adjustable, 1000 lux | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG073 |  | ILLUMINATED SIGN, 'Room in use' | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC076 |  | SWITCH, 'Room in use' illuminated sign. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRA183 |  | TRACK, curtain, two sided, 2600W 2800D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA318 |  | CHAIR, upright, with arms, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COU010 |  | COUCH, examination/treatment, (3 section), variable height, retractable wheels, with paper roll holder | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL020 |  | HOLDER, sharps box, up to 7 litre capacity, rail/trolley hang or wall mounted, 170H 125W 100D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT002 |  | TROLLEY, modular storage, single open frame, including handle and worktop, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | C0237
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | C0237 |  |  |  |  | Consulting/examination room: double-sided couch access
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | TAB177 |  | TABLE, 720H 900W 700D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | C0522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | C0522 |  |  |  |  | Examination/physical therapy room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Examinations of the patient may be carried out from one or both sides of the couch. 2) Physical therapy is undertaken. 3) Monitoring/diagnostic or therapeutic equipment may be used. 4) Sterile supplies and consumables are stored on a trolley. 5) Electronic patient records (EPRs) may be accessed and updated. 6) Clinical hand washing. 7) Carrying out examinations and assessment of patient. 8) Patient may undress/dress in privacy. 9) Computer workstation(s) may be used. 10) Carrying out non invasive procedures from one or both sides of a couch or plinth. 11) Call systems may be used. 12) Medical hand sanitizer may be used. 13) Hanging outdoor clothing. 14) Dispensing disposable aprons. 15) Dispensing disposable gloves. 16) Telephone(s) may be used.
| Personnel: | [6 empty] | 1 x patient. 1-2 x staff. 1 x other (escort).
| Planning Relationships: | [5 empty] | Close to consultation room(s).
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | This room includes a 3-section couch, alternatively, it may accommodate a 2-section couch or specialist treatment chair. The call repeat lamp is situated over the door outside the room. The following items are shown on the room layout but are optional: - patient/staff call (although expected where a patient will be left unattended); - room in use switch and indicator; - clinical workstation; - location of the privacy curtain (may be at door entrance, as shown, or between couch and clinical workstation, see HBN 00-03). A door and a half will be required if trolley access is required. Piped medical gases may be required for some clinical specialties. Workstations have been placed in at 900mmm. Local policy may prefer a worktop up to 1200mm to facilitate working practice. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
C0522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | C0522 |  |  |  |  | Examination/physical therapy room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 1000
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
| Standby Lighting Grade - Local Lighting: | [13 empty] | A
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | C0522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | C0522 |  |  |  |  | Examination/physical therapy room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | C0522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | C0522 |  |  |  |  | Examination/physical therapy room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL003 |  | PUSH BUTTON, patient/staff call (help) with socket for patient hand-held unit | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG053 |  | LUMINAIRE, examination, ceiling, adjustable, 1000 lux | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG073 |  | ILLUMINATED SIGN, 'Room in use' | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW069 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 900W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC076 |  | SWITCH, 'Room in use' illuminated sign. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRA147 |  | TRACK, curtain, door, C-shape | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA302 |  | CHAIR, swivel, height adjustable, medium back, wipeable, 5 star base, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COU010 |  | COUCH, examination/treatment, (3 section), variable height, retractable wheels, with paper roll holder | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT002 |  | TROLLEY, modular storage, single open frame, including handle and worktop, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | D0434-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | D0434-03 |  |  |  |  | Rest room with beverages & snack preparation bay: 20 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Rest and relaxation or sleeping. 2) Small amounts of dry goods are stored in cupboard(s). 3) Holding/ storing food in refrigerator. 4) Crockery and cutlery are washed mechanically. 5) Hand-rinse basin may be used. 6) Consuming beverages, meals and snacks. 7) People preparing beverages, meals and snacks. 8) Telephone may be used and messages taken. 9) Laptop computer(s) may be used.
| Personnel: | [6 empty] | 20 x persons..
| Planning Relationships: | [5 empty] | Staff use - located away from public areas.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 35.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The following items are shown on the room layout but are optional: - telephone outlet; - mini kitchen water boiler; - mini kitchen microwave. The following items may be provided: - cube lockers for personal belongings; - television, radio - generally not in staff rest areas; - water cooler, or access. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
D0434-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | D0434-03 |  |  |  |  | Rest room with beverages & snack preparation bay: 20 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 – 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V/EM
| Daytime General Service Illuminance (Lux): | [13 empty] | 50 |  | Floor
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 200 |  | On tables
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 300 |  | At servery counter
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | D0434-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | D0434-03 |  |  |  |  | Rest room with beverages & snack preparation bay: 20 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | D0434-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | D0434-03 |  |  |  |  | Rest room with beverages & snack preparation bay: 20 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP715 |  | CUPBOARD, base, including sink panel, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP731 |  | CUPBOARD/DRAWER UNIT, base, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT301 |  | OUTLET, cold water for equipment | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP359 |  | TAP, pillar, high neck, long lever, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAT003 |  | WATER BOILER, 2.5 litre, electric, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WRT221 |  | WORKTOP, dished, stainless steel, with integral centre sink bowl and 2 tap holes, 2100W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP252 |  | CUPBOARD, 2 adjustable shelves, wall mounted, 750H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP259 |  | CUPBOARD, space for built in microwave, wall mounted, 750H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | OVE016 |  | OVEN, microwave, capacity 18 litre, build in, (suitable for CUP259) | [16 empty] | 2
| 16 |  |  | 16 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF058 |  | REFRIGERATOR, capacity 160 litre, automatic defrost, stainless steel, underbench, external temperature gauge, lockable, on castors, 850H 610W 600D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB135 |  | TABLE, 710H 1500W 900D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | D1133
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | D1133 |  |  |  |  | Discharge lounge: 8 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 15/04/2013
| Activities: | [5 empty] | 1) Final recovery of patient prior to discharge. 2) Consuming beverages, meals and snacks. 3) Displaying information.
| Personnel: | [6 empty] | 8 x Patients
| Planning Relationships: | [5 empty] | Close to main entrance.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 20 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Loudspeaker, TV/video control situated at reception desk. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
D1133
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | D1133 |  |  |  |  | Discharge lounge: 8 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 15/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 – 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | D1133
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | D1133 |  |  |  |  | Discharge lounge: 8 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 15/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Clear glazing Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | D1133
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | D1133 |  |  |  |  | Discharge lounge: 8 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 15/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT206 |  | SOCKET outlet television aerial, single. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BRA015 |  | BRACKET, flat panel monitor, height adjustable, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | TVM003 |  | TELEVISION monitor, colour, flat panel, large, wall mounted | [16 empty] | 2
| 7 |  |  | 7 |  |  |  |  | CHA391 |  | CHAIR, easy, reclining, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC094 |  | RACK, magazine, double sided, mobile | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TAB109 |  | TABLE, occasional, square | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0171
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0171 |  |  |  |  | Parking bay: large equipment
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Parking equipment. 2) Equipment is placed on charge.
| Personnel: | [6 empty] | Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 4 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
G0171
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0171 |  |  |  |  | Parking bay: large equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | See HVAC notes 2
| Ventilation Type: | [13 empty] | N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
| General Notes: | [5 empty] | Part of corridor space
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0171
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0171 |  |  |  |  | Parking bay: large equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0171
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0171 |  |  |  |  | Parking bay: large equipment
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0180-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0180-01 |  |  |  |  | Parking bay: resusitation trolley
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Mobile equipment may be parked and stored and/or recharged. 2) Equipment is placed on charge. 3) Carrying out routine checks on equipment.
| Personnel: | [6 empty] | Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
G0180-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0180-01 |  |  |  |  | Parking bay: resusitation trolley
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | See HVAC notes 2
| Ventilation Type: | [13 empty] | N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
| General Notes: | [5 empty] | Part of corridor space
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0180-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0180-01 |  |  |  |  | Parking bay: resusitation trolley
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0180-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0180-01 |  |  |  |  | Parking bay: resusitation trolley
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRO310 |  | TROLLEY, emergency/resuscitation, complete with defibrillator, 955H 825W 575D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0180-05
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0180-05 |  |  |  |  | Parking bay: ultrasound unit
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Mobile equipment may be parked and stored and/or recharged. 2) Equipment is placed on charge.
| Personnel: | [6 empty] | Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
G0180-05
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0180-05 |  |  |  |  | Parking bay: ultrasound unit
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | See HVAC notes 2
| Ventilation Type: | [13 empty] | N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
| General Notes: | [5 empty] | Part of corridor space
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0180-05
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0180-05 |  |  |  |  | Parking bay: ultrasound unit
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0180-05
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0180-05 |  |  |  |  | Parking bay: ultrasound unit
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | ULT016 |  | ULTRASOUND sonography with doppler for deep vein thrombosis (DVT) | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0180-06
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0180-06 |  |  |  |  | Parking bay: mobile x-ray unit
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Mobile equipment may be parked and stored and/or recharged. 2) Equipment is placed on charge.
| Personnel: | [6 empty] | Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
G0180-06
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0180-06 |  |  |  |  | Parking bay: mobile x-ray unit
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | See HVAC notes 2
| Ventilation Type: | [13 empty] | N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
| General Notes: | [5 empty] | Part of corridor space
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0180-06
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0180-06 |  |  |  |  | Parking bay: mobile x-ray unit
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0180-06
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0180-06 |  |  |  |  | Parking bay: mobile x-ray unit
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAC197 |  | RACK, x-ray lead apron, 6 swivel arms, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | XRA007 |  | X-RAY IMAGING UNIT, adjustable arm 1840/580mm, electric, mobile, battery driven, 1840H 2240W 660W | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0180-10
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0180-10 |  |  |  |  | Parking bay: 3 wheelchairs
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Mobile equipment may be parked and stored and/or recharged. 2) Equipment is placed on charge.
| Personnel: | [6 empty] | Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
G0180-10
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0180-10 |  |  |  |  | Parking bay: 3 wheelchairs
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | See HVAC notes 2
| Ventilation Type: | [13 empty] | N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
| General Notes: | [5 empty] | Part of corridor space
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0180-10
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0180-10 |  |  |  |  | Parking bay: 3 wheelchairs
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0180-10
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0180-10 |  |  |  |  | Parking bay: 3 wheelchairs
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0407
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0407 |  |  |  |  | Exit/parking bay: theatre: 1 bed/trolley
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Bed(s)/trolley(s) are parked until required to remove patients from the operating theatre.
| Personnel: | [6 empty] | Intermittent use.
| Planning Relationships: | [5 empty] | Direct access from theatre.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
2700 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | The notional layout provides an allowance for an exit bay space to a single operating theatre. Space is required for bed holding, access to rooms and medical gas isolation valves etc but it is a local decision as to design and operationally how this is provided. "IN USE" sign, etc located over theatre door in exit bay. See theatre RDS for component listing. Controls for lighting, heating and medical gas isolation valves should be located here.
| ADB | [7 empty] | Room Environmental Data
G0407
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0407 |  |  |  |  | Exit/parking bay: theatre: 1 bed/trolley
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | See HVAC notes 2
| Ventilation Type: | [13 empty] | Cascade
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
| General Notes: | [5 empty] | Overall extract ventilation dependent on overall pressure regime for operating theatre suites.
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0407
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0407 |  |  |  |  | Exit/parking bay: theatre: 1 bed/trolley
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 3 sets of doors: 2 x personnel & equipment access (1000mm); 1 x personnel, bed, trolley & equipment access (1900mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0407
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0407 |  |  |  |  | Exit/parking bay: theatre: 1 bed/trolley
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0710
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0710 |  |  |  |  | Telephone booth
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Payphone may be used.
| Personnel: | [6 empty] | 1 x person.
| Planning Relationships: | [5 empty] | Within easy access.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 1.5 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | All public telephones should include a shelf to enable a person with a hearing impairment to use a portable text phone. The following items are shown on the room layout but are optional: - acoustic hood. - Where provided, it should be designed and mounted in such a way that it is not a hazard to disabled people i.e. by ensuring that it is located outside any circulation route or by provision of a hazard warning.
| ADB | [7 empty] | Room Environmental Data
G0710
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0710 |  |  |  |  | Telephone booth
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | n/a
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 100
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 300 |  | On telephone
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 43
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 43 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0710
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0710 |  |  |  |  | Telephone booth
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0710
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0710 |  |  |  |  | Telephone booth
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT220 |  | SOCKET, outlet telephone, part of TEL004 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TEL004 |  | TELEPHONE handset coin/card operated, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | TEL019 |  | TELEPHONE HOOD, acoustic, wall mounted | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0712
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0712 |  |  |  |  | Telephone booth: wheelchair accessible
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Payphone may be used.
| Personnel: | [6 empty] | 1 x person.
| Planning Relationships: | [5 empty] | Within easy access.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | Telephones for wheelchair users should be located to enable access from the front and side. This is assumed in the room layout. Where it is only possible to approach the telephone from the front, a knee hole at least 500 mm deep and 700 mm high should be provided This space includes a fold-down seat (450-520 mm high), alternatively, it can accommodate a perch seat (650-800 mm high) for ambulant users only.
| ADB | [7 empty] | Room Environmental Data
G0712
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0712 |  |  |  |  | Telephone booth: wheelchair accessible
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | n/a
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 100
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 300 |  | On telephone
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 44
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 44 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0712
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0712 |  |  |  |  | Telephone booth: wheelchair accessible
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0712
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | G0712 |  |  |  |  | Telephone booth: wheelchair accessible
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT220 |  | SOCKET, outlet telephone, part of TEL004 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | RAI046 |  | RAIL, grab, vertical, wall mounted, 450mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SEA024 |  | SEAT, tip-up, wall mounted, 400 W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TEL004 |  | TELEPHONE handset coin/card operated, wall mounted | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | H1304-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | H1304-02 |  |  |  |  | Seminar room: 20 places (including 1 wheelchair place)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Seminars/conferences are held. 2) Multimedia equipment may be used. 3) Laptop computer(s) may be used. 4) Telephone(s) may be used.
| Personnel: | [6 empty] | 21 x persons (including lecturer). Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 28 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | For flexibility in use, direct access to a store is required. The call repeat lamp is situated over the door outside the room. The following items may be provided: - a TV; - an overhead projector; - video-conferencing facilities; - an induction loop hearing system; - a public address system (in larger seminar rooms); - a clinical wash-hand basin and gel dispenser to allow for clinical use of the room; - audiovisual links to clinical areas for training purposes; - shelving, desks/tables and computers for training use. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
H1304-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | H1304-02 |  |  |  |  | Seminar room: 20 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 100-150 |  | On floor
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 300 |  | Over working plane
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 53
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 53 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | H1304-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | H1304-02 |  |  |  |  | Seminar room: 20 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control. Blinds will be required to darken room, full blackout is rarely required Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | H1304-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | H1304-02 |  |  |  |  | Seminar room: 20 places (including 1 wheelchair place)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 17 |  |  | 17 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT004 |  | OUTLET cable, fused, 13 amp, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 11 |  |  | 11 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT135 |  | SOCKET outlet, computer data, single, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SCR043 |  | SCREEN, projection, ceiling mounted, 1800H 1800W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA006 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 1200H1800W | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | PRO026 |  | PROJECTOR, multi-media, ceiling mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA051 |  | BOARD, flip chart, height adjustable, freestanding | [16 empty] | 3
| 20 |  |  | 20 |  |  |  |  | CHA318 |  | CHAIR, upright, with arms, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP036 |  | CUPBOARD, steel, 2 adjustable shelves, 2 door, lockable, 900H 900W 420D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB008 |  | TABLE, 710H 1200W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | J0232
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J0232 |  |  |  |  | Reception: 2 person
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception and registration of patients. 2) Maintaining appointments and attendance register. 3) Computer workstation(s) may be used. 4) Dealing with enquiries. 5) Telephone(s) may be used. 6) Controlling access to clinical or work area. 7) Staff notices, information and/or messages may be displayed.
| Personnel: | [6 empty] | 2 x staff. 2 x patients/visitors.
| Planning Relationships: | [5 empty] | Close to, with clear view of, entrance and waiting area. Close to self-registration point when provided. Close to clinical or work area(s). Easy access to records store when paper records are still used. Access to a "safe haven" area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 11 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | The reception desk should be accessible to all users and provide security for staff. In facilities for children and young people it should be child friendly. The following items may be provided: - a printer; - a "controlled entry" system; - a "next patient" call system; . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
J0232
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J0232 |  |  |  |  | Reception: 2 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 500 |  | Over desk task area
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 58
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 58 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | J0232
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J0232 |  |  |  |  | Reception: 2 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | J0232
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J0232 |  |  |  |  | Reception: 2 person
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | COU087 |  | COUNTER RECEPTION, console top, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PAN063 |  | PANEL, indicator | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | J1155
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J1155 |  |  |  |  | Waiting area: 20 places (including 2 wheelchair places)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patients, relatives and escorts wait to be seen. 2) Displaying information.
| Personnel: | [6 empty] | 20 x persons, including 2 x wheelchair user
| Planning Relationships: | [5 empty] | Adjacent to reception area. Close to clinical or work area. Close to WC facilities.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 30 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Type of seating to be suitable for patient profile. Method for calling patients into clinical rooms to be decided locally. The following items may be provided: - an enclosed noticeboard; - background music and other entertainment facilities; - television and internet access.
| ADB | [7 empty] | Room Environmental Data
J1155
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J1155 |  |  |  |  | Waiting area: 20 places (including 2 wheelchair places)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | -
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 63
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 63 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | J1155
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J1155 |  |  |  |  | Waiting area: 20 places (including 2 wheelchair places)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control or Not applicable Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | J1155
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J1155 |  |  |  |  | Waiting area: 20 places (including 2 wheelchair places)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAC089 |  | RACK, leaflet/pamphlet, 4 sections, with adjustable dividers, wall mounted, 300H 805W 215D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | RAC091 |  | RACK, magazine, 3 shelves, floor standing, fixed to the wall, 1400H 900W 300D | [16 empty] | 2
| 3 |  |  | 3 |  |  |  |  | CHA367 |  | UNIT CHAIR, 1 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA368 |  | UNIT CHAIR, 2 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA369 |  | UNIT CHAIR, 3 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | J1155-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J1155-01 |  |  |  |  | Waiting area: 15 places (including 1wheelchair place)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patients, relatives and escorts wait to be seen. 2) Displaying information.
| Personnel: | [6 empty] | 15 x persons, including 1 x wheelchair user.
| Planning Relationships: | [5 empty] | Adjacent to reception area. Close to clinical or work area. Close to WC facilities.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 22.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Type of seating to be suitable for patient profile. Method for calling patients into clinical rooms to be decided locally. The following items may be provided: - an enclosed noticeboard; - background music and other entertainment facilities; - television and internet access.
| ADB | [7 empty] | Room Environmental Data
J1155-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J1155-01 |  |  |  |  | Waiting area: 15 places (including 1wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | -
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 64
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 64 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | J1155-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J1155-01 |  |  |  |  | Waiting area: 15 places (including 1wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control or Not applicable Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | J1155-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J1155-01 |  |  |  |  | Waiting area: 15 places (including 1wheelchair place)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAC089 |  | RACK, leaflet/pamphlet, 4 sections, with adjustable dividers, wall mounted, 300H 805W 215D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | RAC091 |  | RACK, magazine, 3 shelves, floor standing, fixed to the wall, 1400H 900W 300D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CHA367 |  | UNIT CHAIR, 1 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA368 |  | UNIT CHAIR, 2 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA369 |  | UNIT CHAIR, 3 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | J1255
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J1255 |  |  |  |  | Waiting area: 5 places (including 1 wheelchair place)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patients, relatives and escorts wait to be seen. 2) Displaying information.
| Personnel: | [6 empty] | 5 x persons, including 1 x wheelchair user
| Planning Relationships: | [5 empty] | Close to clinical or work area. Close to WC facilities.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 9 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design. .
| Notes: | [7 empty] | Type of seating to be suitable for patient profile. Method for calling patients into clinical rooms to be decided locally. The following items may be provided: - an enclosed noticeboard; - background music and other entertainment facilities; - television and internet access.
| ADB | [7 empty] | Room Environmental Data
J1255
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J1255 |  |  |  |  | Waiting area: 5 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | -
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 65
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 65 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | J1255
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J1255 |  |  |  |  | Waiting area: 5 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control or Not applicable Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | J1255
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J1255 |  |  |  |  | Waiting area: 5 places (including 1 wheelchair place)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAC089 |  | RACK, leaflet/pamphlet, 4 sections, with adjustable dividers, wall mounted, 300H 805W 215D | [16 empty] | 2
| 4 |  |  | 4 |  |  |  |  | CHA367 |  | UNIT CHAIR, 1 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | J1414-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J1414-01 |  |  |  |  | Play area: 5 children
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Children accompanying relatives or waiting to be seen are able to play. 2) Toys, books and games are stored.
| Personnel: | [6 empty] | 5 x children.
| Planning Relationships: | [5 empty] | Off, and observable from, the waiting area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 7.5 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
J1414-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J1414-01 |  |  |  |  | Play area: 5 children
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/EM
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 69
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 69 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | J1414-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J1414-01 |  |  |  |  | Play area: 5 children
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control. Window opening restrictors max 100mm at bottom Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Desirable - Project Option Clear safety glass when provided Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | J1414-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | J1414-01 |  |  |  |  | Play area: 5 children
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BIN007 |  | BIN, storage, complete with drop on lid, mobile, 550H 610W 510D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA335 |  | CHAIR, child, upright, stacking, seat height 380, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB060 |  | TABLE, child, 470H 1200W 700D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1308
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | L1308 |  |  |  |  | Near patient testing room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Electronic patient records (EPRs) may be accessed and updated. 2) Clinical wash-hand basin may be used. 3) Patient records may be reviewed and recorded. 4) Performing electrolyte analysis. 5) Performing blood gas analysis. 6) Performing glucose analysis. 7) Computer workstation(s) may be used. 8) Displaying information. 9) Printer may be used.
| Personnel: | [6 empty] | 2 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | This room is based on the use of an outward opening entrance door, where an entrance door is not provided, the entrance must be within a secure staff area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Type of analyser provided to suit range of tests to be undertaken. The following items are shown on the room layout but are optional: - door to room; - a specimen fridge; - a sink and demineralised water supply. The following items may be provided: - a pneumatic tube to/from pathology. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
L1308
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | L1308 |  |  |  |  | Near patient testing room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1308
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | L1308 |  |  |  |  | Near patient testing room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. Not applicable or 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1308
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | L1308 |  |  |  |  | Near patient testing room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWB080 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 2000W 750D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWS190 |  | WORKTOP, with right hand sink bowl (sink size 200x450x365), 920H 3000W 750D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC023 |  | CABINET, upper, modular storage, for 400 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP022 |  | TAP, laboratory, cold water | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP023 |  | TAP, laboratory, hot water | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | ANA052 |  | ANALYSER, blood gas with electrolytes, 550H 700W 530D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA303 |  | CHAIR, swivel, height adjustable 540-790, tilting back, adjustable footrest, wipeable, 5 star base, on castors/glides | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF060 |  | REFRIGERATOR, reagents, capacity 110 litre, external temperature gauge, automatic defrost, underbench, 850H 500W 590D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT001 |  | TROLLEY, modular storage, single open frame, including handle, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1804-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | L1804-01 |  |  |  |  | Service room: clinical equipment
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Electronic and Medical Engineering (EME) equipment may be serviced or repaired. 2) Minor scheduled/unscheduled servicing of equipment may be undeertaken by a visiting EME technician when full facilities of EME workshop are not required. 3) User servicing and instruction manuals for EME equipment are stored. 4) Computer workstation(s) may be used. 5) Telephone(s) may be used. 6) Piped medical gases, vacuum and associated equipment may be used. 7) Secure storage. 8) Clinical hand washing.
| Personnel: | [6 empty] | Up to 2 x staff. Intermittent use
| Planning Relationships: | [5 empty] | Good vision of the interior of this room is essential for the safety of the servicing personnel. Direct access from Dirty Utility. Direct access to Clinical equipment Store.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
L1804-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | L1804-01 |  |  |  |  | Service room: clinical equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 500 |  | Bench
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | non-ionising if radiation present
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1804-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | L1804-01 |  |  |  |  | Service room: clinical equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 3 sets of doors: 1 x personnel, wheelchair & equipment access (1000mm); 2 x personnel, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1804-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | L1804-01 |  |  |  |  | Service room: clinical equipment
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT454 |  | OUTLET, 7 kPa compressed air, surgical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT461 |  | OUTLET, nitrous oxide, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT480 |  | OUTLET, gas scavenging (AGS), medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE201 |  | SHELF, 600W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE211 |  | SHELF, 900W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW090 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 3000W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC062 |  | EMERGENCY STOP switch button, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Clinical administration. 2) Computer workstation(s) may be used. 3) Telephone(s) may be used. 4) Discussions and interviews may take place. 5) Files and records are stored. 6) Hanging outdoor clothing. 7) Secure holding/storing of clothing and personal belongings. 8) Printer may be used. 9) Electronic patient records (EPRs) may be accessed and updated. 10) Staff notices, information and/or messages may be displayed. 11) Dealing with enquiries. 12) Information on computers may be accessed.
| Personnel: | [6 empty] | 1 x staff Up to x 2 others.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following equipment is shown on the room layout but is optional: - call repeat lamps for controlled drugs cupboards (but required if the office is used for clinical control). The following items may provided; - shelving; - printer. The following items may be provided if the office is used for clinical control: - a small safe; - a key cupboard; - an alarm panel, see HTM 08-03; - a dimming switch - recommended if the room is used for viewing digital images. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 3 |  |  | 3 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG138 |  | LUMINAIRE, indicating controlled drugs cupboard repeat | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB049 |  | CABINET, lateral filing, 6 rails, 2 door, 1970H 1000W 470D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DES026 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1400W 700D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA057 |  | DRAWER UNIT, 3 drawer, lockable, on castors, desk height 715H 430W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0252-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0252-02 |  |  |  |  | Office: 3 person
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Clinical administration. 2) Computer workstation(s) may be used. 3) Telephone(s) may be used. 4) Discussions and interviews may take place. 5) Files and records are stored. 6) Hanging outdoor clothing. 7) Secure holding/storing of clothing and personal belongings.
| Personnel: | [6 empty] | 3 x staff. Up to 3 x others.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 18 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following equipment is shown on the room layout but is optional: - call repeat lamps for controlled drugs cupboards (but required if the office is used for clinical control). The following items may be provided if the office is used for clinical control: - a dimming switch - recommended if the room is used for viewing digital images. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0252-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0252-02 |  |  |  |  | Office: 3 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0252-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0252-02 |  |  |  |  | Office: 3 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0252-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0252-02 |  |  |  |  | Office: 3 person
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 5 |  |  | 5 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG138 |  | LUMINAIRE, indicating controlled drugs cupboard repeat | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB049 |  | CABINET, lateral filing, 6 rails, 2 door, 1970H 1000W 470D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | DES026 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1400W 700D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | DRA057 |  | DRAWER UNIT, 3 drawer, lockable, on castors, desk height 715H 430W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0254
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0254 |  |  |  |  | Office: 4 person
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Clinical administration. 2) Computer workstation(s) may be used. 3) Telephone(s) may be used. 4) Files and records are stored. 5) Hanging outdoor clothing. 6) Secure holding/storing of clothing and personal belongings. 7) Printer may be used. 8) Electronic patient records (EPRs) may be accessed and updated. 9) Information on computers may be accessed. 10) Staff notices, information and/or messages may be displayed.
| Personnel: | [6 empty] | 4 x staff. Up to 4 x others.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 24 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The following equipment is shown on the room layout but is optional: - call repeat lamps for controlled drugs cupboards (but required if the office is used for clinical control). The following items may be provided if the office is used for clinical control: - a dimming switch - recommended if the room is used for viewing digital images. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0254
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0254 |  |  |  |  | Office: 4 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0254
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0254 |  |  |  |  | Office: 4 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0254
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0254 |  |  |  |  | Office: 4 person
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 5 |  |  | 5 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG138 |  | LUMINAIRE, indicating controlled drugs cupboard repeat | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CAB049 |  | CABINET, lateral filing, 6 rails, 2 door, 1970H 1000W 470D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | DES026 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1400W 700D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | DRA057 |  | DRAWER UNIT, 3 drawer, lockable, on castors, desk height 715H 430W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0326-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0326-01 |  |  |  |  | Office: technical and data review: 2 workstations
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Stored data and/or images may be archived, retrieved or distributed. 2) Test reports may be prepared. 3) Electronic patient records (EPRs) may be accessed and updated. 4) Staff notices, information and/or messages may be displayed. 5) Telephone(s) may be used.
| Personnel: | [6 empty] | 2 x staff. 1 x other.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | A dimming switch is recommended if the room is used for viewing digital images. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0326-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0326-01 |  |  |  |  | Office: technical and data review: 2 workstations
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0326-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0326-01 |  |  |  |  | Office: technical and data review: 2 workstations
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0326-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0326-01 |  |  |  |  | Office: technical and data review: 2 workstations
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 3 |  |  | 3 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | WRT065 |  | WORKTOP, non-clinical, 1500W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB027 |  | CABINET, filing, 2 drawer, 710H 800W 470D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0410
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0410 |  |  |  |  | Photocoping/printing room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Carrying out printing activities. 2) Carrying out photocopying activities. 3) Shredding documents. 4) Stationery/paper is stored.
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Within an administration space.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 6 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | One photocopy/printing room, with multifunctional printer/copier and storage for paper/printing supplies, for every 32 workstations. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0410
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0410 |  |  |  |  | Photocoping/printing room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0410
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0410 |  |  |  |  | Photocoping/printing room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0410
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0410 |  |  |  |  | Photocoping/printing room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP036 |  | CUPBOARD, steel, 2 adjustable shelves, 2 door, lockable, 900H 900W 420D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | PRI010 |  | PRINTER multifunction, network, floor standing | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SHR001 |  | SHREDDER, paper | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0724
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0724 |  |  |  |  | Interview room: 4 places (including 1 wheelchair place)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Discussions and interviews may take place. 2) Telephone(s) may be used. 3) Laptop computer(s) may be used. 4) Call systems may be used.
| Personnel: | [6 empty] | Up to 4 x persons.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items are shown on the room layout but are optional: - staff emergency call (not required if the room is for staff use only); - telephone (should not be provided in rooms intended as quiet spaces); - room in use switch and indicator. The following items may be provided: - a clinical wash-hand basin and gel dispenser to allow for clinical use of the room; . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0724
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0724 |  |  |  |  | Interview room: 4 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0724
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0724 |  |  |  |  | Interview room: 4 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0724
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0724 |  |  |  |  | Interview room: 4 places (including 1 wheelchair place)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG073 |  | ILLUMINATED SIGN, 'Room in use' | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC076 |  | SWITCH, 'Room in use' illuminated sign. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0727
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0727 |  |  |  |  | Interview room: 7 places (including 1 wheelchair place)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Discussions and interviews may take place. 2) Telephone(s) may be used. 3) Laptop computer(s) may be used. 4) Call systems may be used.
| Personnel: | [6 empty] | Up to 7 x persons.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items are shown on the room layout but are optional: - staff emergency call (not required if the room is for staff use only); - telephone (should not be provided in rooms intended as quiet spaces); - room in use switch and indicator. The following items may be provided: - a clinical wash-hand basin and gel dispenser to allow for clinical use of the room; . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0727
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0727 |  |  |  |  | Interview room: 7 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0727
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0727 |  |  |  |  | Interview room: 7 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0727
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | M0727 |  |  |  |  | Interview room: 7 places (including 1 wheelchair place)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG073 |  | ILLUMINATED SIGN, 'Room in use' | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC076 |  | SWITCH, 'Room in use' illuminated sign. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA311 |  | SOFA CHAIR, 2 seater, easy, with arms, fully upholstered, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | N0107
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | N0107 |  |  |  |  | Operating theatre: general
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 03/10/2011
| Activities: | [5 empty] | 1) Patient may be connected to anaesthetic machine. 2) Assembling and connecting mobile equipment. 3) Surgical instruments on instrument trolley may be used. 4) Surgical procedures may be performed under local or general anaesthetic. 5) Viewing film and/or computer generated images. 6) Used swabs may be checked, weighed and recorded. 7) Operating lists may be displayed. 8) Recording patient data/notes. 9) Patient is transferred from operating table to bed/trolley. 10) Information on computers may be accessed. 11) Electronic patient records (EPRs) may be accessed and updated. 12) Maintenance of general anaesthesia. 13) Mobile image intensifier may be used. 14) Monitoring/diagnostic or therapeutic equipment may be used.
| Personnel: | [6 empty] | 1 x patient. Up to 7 x staff.
| Planning Relationships: | [5 empty] | Direct access to preparation room. Direct access to anaesthesia room (when provided). Direct access or adjacent to scrub-up room. Direct access to utility room. Direct access to corridor/exit bay.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 48 |  |  |  |  | Height (mm): |  |  |  | 3000
3000 mm is a nominal height; actual height subject to design, local equipment and environmental considerations.
| Notes: | [7 empty] | When laser surgery and X-rays are being undertaken, safety precautions should be employed, including the provision of warning lights located in the corridor above the theatre doors, which will be activated prior to laser surgery or X-rays being undertaken. Requirements for radiation protection of walls and doors together with inclusion of "radiation in use" warning lamps installed at eye level outside the entrance(s) to the room should be subject to RPA advice. Theatre control panel should be flush mounted and ideally should be accessible for maintenance from outside the theatre. "IN USE" sign sited outside the doorway of the room. The following items are shown on the room layout but are optional: The following items may be provided: - anaesthetic machine may be located on a dedicated medical supply unit - project team option; -ceiling mounted hoist for transfer to and from the operating table. Consideration must be given to co-ordination of the hoist with other fixing/services. For dedicated maternity use: - surgical and medical air may be omitted from pendant services. - AGS may be omitted from pendant services subject to local risk assessment. - medical oxygen may be reduced to 1 outlet and/if so the 2 x nitrous oxide outlets are replaced by 1 x nitrous oxide/oxygen mixture. - this RDS assume that a separate resuscitation room is available immediately outside of the theatre. Consideration may be given to providing this service within or en-suite to the theatre when dedicated for maternity use and subject to appropriate review of the ventilation requirements. Outlets defined as voice or data will be the same for structured cabling solutions.
| ADB | [7 empty] | Room Environmental Data
N0107
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | N0107 |  |  |  |  | Operating theatre: general
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 03/10/2011
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 25
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | 25 pascals
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
| General Notes: | [5 empty] | Refer to HTM03-01
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 1000
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 500
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 10000 to 100000
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
| Standby Lighting Grade - Local Lighting: | [13 empty] | A
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40 |  | The LAmax,f dB noise limit applies at any time.
| Noise Intrusion (dB) 1hr night: | [13 empty] | 40
| Noise Intrusion (dB) f night: | [13 empty] | 50
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Duct mounted on Supply
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | N0107
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | N0107 |  |  |  |  | Operating theatre: general
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 03/10/2011
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 4 sets of doors: 2 x personnel & equipment access (1000mm); 2 x personnel, bed, trolley & equipment access (1900mm)
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control For laser or urology surgery see HBN26 Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | N0107
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | N0107 |  |  |  |  | Operating theatre: general
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 03/10/2011
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | LIG031 |  | LUMINAIRE, operating theatre, table with satellite, shadowless, lux 140000 and lux 110000 | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | LIG071 |  | ILLUMINATED SIGN 'RADIATION ON', wall mounted | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | LIG072 |  | ILLUMINATED SIGN "LASER IN USE" | [16 empty] | 1
| 25 |  |  | 25 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 9 |  |  | 9 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT454 |  | OUTLET, 7 kPa compressed air, surgical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT461 |  | OUTLET, nitrous oxide, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT480 |  | OUTLET, gas scavenging (AGS), medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PAN056 |  | PANEL, control surgical procedure room 900H x 1200W: comprises: 1x Operating lamp ON/OFF switch; 1x Emergency battery lighting"ON"; indicating; 3x General lighting ON/OFF including dimmer switch lamp 1x Standby generator electric mains "ON" indicating lamp; 1x Air temperature indicating gauge 1x Air temperature control 1x Humidity indicating gauge 1x Humidity control and indicating lamp; 1x Ventilation plant "ON"; (NORMAL) indicating lamp 1x Indicating lamp "FILTER REPLACE" 1x Indicating lamp "LOW AIR FLOW"; 1x Indicating lamp "MEDICAL GAS FAILURE" 1x Air sampling grille and duct with temperature and humidity sensors; 1x Clock time elapsed 1x Clock synchronous (time of day) 1x Telephone outlet (splash proof) 1x Room "IN USE"; light, ON/OFF switch 1x Room "IN USE"; light, ON/OFF switch 1x Illuminator, x-ray film fixed 1x Illuminator, x-ray film, ON/OFF switch | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | PEN042 |  | PENDANT, electrical services and medical gases, 2 articulated arms, with docking system, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW069 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 900W 700D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SUC002 |  | SUCTION UNIT, pipeline, high pressure, theatre | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | N0107
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | N0107 |  |  |  |  | Operating theatre: general
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 03/10/2011
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | ANA004 |  | ANAESTHETIC MACHINE/WORKSTATION with ventilator, with accessories, mobile, 1580H 565W 695D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA324 |  | CHAIR, anaesthetist, wipeable, height adjustable. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM047 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, touch screen, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL014 |  | HOLDER, sack, with lid foot operated, large, capacity 120 litre, mobile | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | KIC001 |  | KICKABOUT, bowl stand, stainless steel, 360mm dia. | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | PLA002 |  | PLATFORM, step-stand, stackable, portable, 130H 480W 330D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SCA012 |  | SCALE, swab, includes Mains adaptor | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | STA101 |  | STAND, lotion bowl, single, stainless steel, (Bowls not included) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STA102 |  | STAND, 2 lotion bowls, stainless steel, (Bowls not included). | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | STA142 |  | STAND, infusion, twin hook, breaks, mobile | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | STO006 |  | STOOL, surgeon/anaesthetist, height adjustable, includes anti-static seat pads | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB077 |  | TABLE, surgical procedures, radiotranslucen,t o/a 1005H 2100W 835D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | TRO133 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 750W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO201 |  | TROLLEY, instruments, stainless steel, buffered, 870H 920W 620D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO204 |  | TROLLEY instrument tray MAYO, 650W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | N0224
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | N0224 |  |  |  |  | Scrub-up and gowning bay: 3 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Staff are able to scrub up within sight of clock. 2) Donning sterile gowns and gloves, from a trolley, assisted by a circulating nurse. 3) Donning protective apron and face mask. 4) Dispensing disposable aprons. 5) Holding/storing sterile gown packs for one surgical session with a stock of glove packs and masks. 6) Disposal of pack wrappers and paper towels. 7) Operating lists may be displayed.
| Personnel: | [6 empty] | Up to 4 staff.
| Planning Relationships: | [5 empty] | The scrub-up and gowning bay is intended as a recess off the theatres. There is no door between this space and the operating theatre but there may be a direct door from the preparation subject to space and consideration of safe access.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 7 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | Shelving specification to be appropriate for theatre environment. The following items are shown on the room layout but are optional: - shelving which may be replaced by a supplies trolley with or without a top for opening gowning packs. The following items may be provided: - sterile glove dispenser, assume to be stored on the shelving but may be located in a wall mounted dispenser; - lead apron rack.
| ADB | [7 empty] | Room Environmental Data
N0224
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | N0224 |  |  |  |  | Scrub-up and gowning bay: 3 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Duct mounted on Supply
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | N0224
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | N0224 |  |  |  |  | Scrub-up and gowning bay: 3 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. Not applicable or 1 doorset: 1 x personnel access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | N0224
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | N0224 |  |  |  |  | Scrub-up and gowning bay: 3 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SHE212 |  | SHELF, 900W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRO603 |  | TROUGH scrub-up, hospital pattern, stainless steel, triple, 75mm upstand, 950H 2400W 450D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | DIS006 |  | DISPENSER, disposable nailbrush, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | P0625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | P0625 |  |  |  |  | Pantry/refreshment area
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Preparing beverages/snacks with patients. 2) Microwave oven may be used. 3) Small amounts of dry goods are stored in cupboard(s). 4) Provision of refrigerated storage. 5) Trays, crockery and cutlery are stored. 6) Disposal of waste and contaminated materials. 7) Hand-rinse basin may be used.
| Personnel: | [6 empty] | 1 - 2 x persons. Intermittent use.
| Planning Relationships: | [5 empty] | Located in staff, patient or visitors areas as appropriate.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following items are included on the room layout but are optional: - a microwave oven; - a dishwasher. The layout is suitable for ambulant/semi-ambulant users, consideration must be given to wheelchair user provision.
| ADB | [7 empty] | Room Environmental Data
P0625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | P0625 |  |  |  |  | Pantry/refreshment area
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | -
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Heat
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | P0625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | P0625 |  |  |  |  | Pantry/refreshment area
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | P0625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | P0625 |  |  |  |  | Pantry/refreshment area
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS015 |  | BASIN, small, stainless steel, apron front, 1 tap hole, 500W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP703 |  | CUPBOARD, base, with door, on plinth, 900H 400W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP715 |  | CUPBOARD, base, including sink panel, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CUP731 |  | CUPBOARD/DRAWER UNIT, base, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CUP753 |  | CUPBOARD, upper, with door, 600H 600W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT301 |  | OUTLET, cold water for equipment | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT341 |  | OUTLET, drainage, anti-syphon | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP359 |  | TAP, pillar, high neck, long lever, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAT003 |  | WATER BOILER, 2.5 litre, electric, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WRT237 |  | WORKTOP, dished, stainless steel, with integral left of centre sink bowl and 2 tap holes, 3500W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS007 |  | DISPENSER, paper towel roll, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | WAS065 |  | DISHWASHER, under bench, high temperature | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | OVE013 |  | OVEN, microwave, heavy duty, 1600watt, capacity 26 litre, 370H 465W 560D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF058 |  | REFRIGERATOR, capacity 160 litre, automatic defrost, stainless steel, underbench, external temperature gauge, lockable, on castors, 850H 610W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | S0012
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | S0012 |  |  |  |  | Infant feeding room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Mother breast or bottle feeding her baby. 2) Mother to express milk using breast pump. 3) Wash-hand basin may be used.
| Personnel: | [6 empty] | 1 x infant. 1 x parent/carer.
| Planning Relationships: | [5 empty] | Easy access from waiting area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 6 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | Expressed milk must be stored elsewhere.
| ADB | [7 empty] | Room Environmental Data
S0012
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | S0012 |  |  |  |  | Infant feeding room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E/N
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | S0012
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | S0012 |  |  |  |  | Infant feeding room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | S0012
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | S0012 |  |  |  |  | Infant feeding room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS107 |  | BASIN, medium, general pattern, vitreous china, 2 tap holes, no overflow, bottom outlet, 500W 400D. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA306 |  | CHAIR, easy, low back, with open arms, upholstered, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | T0211
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | T0211 |  |  |  |  | Staff communication base: 2 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Electronic patient records (EPRs) may be accessed and updated. 2) Computer workstation(s) may be used. 3) Dealing with enquiries. 4) Telephone(s) may be used. 5) Staff supervise and observe patients. 6) Carrying out administration and clerical duties. 7) Information may be provided to patients, carers and visitors. 8) Clinical administration. 9) Patient records may be reviewed and recorded. 10) Information on computers may be accessed. 11) Call systems may be used.
| Personnel: | [6 empty] | 2 x staff. 2 x other staff or patients/visitors.
| Planning Relationships: | [5 empty] | Situated to allow easy access and good observation of the areas served. Access to a "safe haven" area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 11 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | Clear access space around the staff communication base should be maintained even when someone is standing at the front of the base. The following items are shown on the room layout but are optional: - call system alarm panel, see HTM 08-03; The following items may be provided: - controlled drugs cupboard alarm; - departmental controlled entry system. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
T0211
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | T0211 |  |  |  |  | Staff communication base: 2 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
| Nighttime General Service Illuminance (Lux): | [13 empty] | 30-200
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
| Standby Lighting Grade - Local Lighting: | [13 empty] | A
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | T0211
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | T0211 |  |  |  |  | Staff communication base: 2 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | T0211
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | T0211 |  |  |  |  | Staff communication base: 2 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | COU087 |  | COUNTER RECEPTION, console top, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PAN063 |  | PANEL, indicator | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | T0522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | T0522 |  |  |  |  | Preparation room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Trays are prepared and trolleys laid up for surgical/clinical procedures. 2) Sterile pre-set trays are held/stored 3) Sterile equipment, consumable supplies and packs are stored. 4) Non-sterile medical items, equipment and supplies are stored. 5) Sterile fluids are stored. 6) Instrument trolleys are held/stored. 7) Storing sundries and small items.
| Personnel: | [6 empty] | 2-3 x staff.
| Planning Relationships: | [5 empty] | Direct access to operating theatre. Access from corridor for delivery of supplies.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The number and size of dressing/instrument trolleys is a project team option. The following items are shown on the room layout but are optional: - heated lotion cabinet which could be provided in a central store instead of within the preparation room. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
T0522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | T0522 |  |  |  |  | Preparation room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | >25
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | 35 pascals
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40 |  | The LAmax,f dB noise limit applies at any time.
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | 50
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | T0522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | T0522 |  |  |  |  | Preparation room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control, security control as necessary, see BS2881 Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | T0522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | T0522 |  |  |  |  | Preparation room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SMC051 |  | CABINET, tall, modular storage, for 600 facing inserts, open, on plinth, 2100H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW025 |  | WORKTOP, clinical, for 600 facing modular storage cabinets, 1500W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAB036 |  | CABINET warming, lotion, 48x1 litre, 1320H 620W 630D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SMF011 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 465D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STA102 |  | STAND, 2 lotion bowls, stainless steel, (Bowls not included). | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO133 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 750W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO201 |  | TROLLEY, instruments, stainless steel, buffered, 870H 920W 620D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | T0535
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | T0535 |  |  |  |  | Clean utility room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Dressing/instrument trolleys are held and prepared. 2) Sterile supplies and consumables are held. 3) Controlled and scheduled drugs are stored securely. 4) Non-controlled medicines and pharmaceuticals are stored securely. 5) Infusion fluids are stored. 6) Provision of refrigerated storage. 7) Flammable medicines are stored. 8) Supplies trolleys are held/stored. 9) Clinical wash-hand basin may be used. 10) Bar coded items may be tracked. 11) Medication is prepared for administration. 12) Contrast media, I.V. injections and other sterile procedures may be prepared. 13) Trolleys for clinical procedures are prepared and laid up. 14) Sterile packs, lotions and drugs may be prepared for immediate use. 15) Computer workstation(s) may be used.
| Personnel: | [6 empty] | 2 x staff.
| Planning Relationships: | [5 empty] | Close to clinical area, particularly treatment rooms.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 16 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | See BS 2881 for requirements for medicines storage. See Misuse of Drugs (Safe Custody) Regulations for requirements for scheduled/controlled drugs storage. The following items may be provided: - a barcode reader and charger. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
T0535
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | T0535 |  |  |  |  | Clean utility room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 150
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | T0535
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | T0535 |  |  |  |  | Clean utility room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control, security control as necessary, see BS2881 Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | T0535
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | T0535 |  |  |  |  | Clean utility room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT050 |  | OUTLET, controlled drugs cupboard | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT056 |  | CONNECTION UNIT, unswitched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC003 |  | CABINET, tall, modular storage, for 400 facing inserts, with door, on plinth, 2100H | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC023 |  | CABINET, upper, modular storage, for 400 facing inserts, with door, 750H | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC051 |  | CABINET, tall, modular storage, for 600 facing inserts, open, on plinth, 2100H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW056 |  | WORKTOP, clinical, for 6 x 400 facing modular storage cabinets, 2730W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAB064 |  | CABINET, metal, controlled drugs, 1 door, lockable, with warning light, wall mounted, 550H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | SMF011 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 465D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP550 |  | CUPBOARD, flammable material, metal, adjustable spillage tray and sump, lockable, 712H 355W 305D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF059 |  | REFRIGERATOR, medical (drug/vaccine), capacity 160 litre, external temperature gauge, automatic defrost, lockable, underbench, 850H 550W 620D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT011 |  | TROLLEY, modular storage, single open frame, including handles, with up to 10 sets of runners for 400 facing inserts, 1500H 600W 650D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | T0540
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | T0540 |  |  |  |  | Medicine store/preparation room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Medication is prepared for administration. 2) Controlled and scheduled drugs are stored securely. 3) Non-controlled medicines and pharmaceuticals are stored securely. 4) Provision of refrigerated storage. 5) Flammable medicines are stored. 6) Clinical wash-hand basin may be used. 7) Bar coded items may be tracked. 8) Computer workstation(s) may be used. 9) Telephone(s) may be used.
| Personnel: | [6 empty] | 1 x staff.
| Planning Relationships: | [5 empty] | Close to clinical area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | See BS 2881 for requirements for medicines storage. See Misuse of Drugs (Safe Custody) Regulations for requirements for scheduled/controlled drugs storage. The following items may be provided: - a barcode reader and charger. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
T0540
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | T0540 |  |  |  |  | Medicine store/preparation room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | T0540
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | T0540 |  |  |  |  | Medicine store/preparation room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control, security control as necessary, see BS2881 Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | T0540
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | T0540 |  |  |  |  | Medicine store/preparation room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT050 |  | OUTLET, controlled drugs cupboard | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT056 |  | CONNECTION UNIT, unswitched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC001 |  | CABINET, tall, modular storage, for 400 facing inserts, open, on plinth, 2100H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC023 |  | CABINET, upper, modular storage, for 400 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW081 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 2100W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAB064 |  | CABINET, metal, controlled drugs, 1 door, lockable, with warning light, wall mounted, 550H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP550 |  | CUPBOARD, flammable material, metal, adjustable spillage tray and sump, lockable, 712H 355W 305D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF059 |  | REFRIGERATOR, medical (drug/vaccine), capacity 160 litre, external temperature gauge, automatic defrost, lockable, underbench, 850H 550W 620D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0554-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0554-03 |  |  |  |  | Staff communal changing room: 30 lockers
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) User may undress and dress. 2) Changing into clean uniforms (including blues or greens). 3) Changing footwear. 4) Secure hanging of wet outdoor clothing. 5) Secure holding/storing of clothing and personal belongings. 6) Secure holding/storage of motorcycle and bicycle helmets. 7) Hanging outdoor clothing. 8) Disposal of dirty uniforms.
| Personnel: | [6 empty] | Up to 12 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Direct access to showers and/or individual changing room(s). Close to WCs. Close to uniform exchange, if provided.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 30 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | It is assumed that this space is supported by one individual changing room. See V0725 for details of semi-ambulant individual changing room and V0276 for independent wheelchair individual changing room. The room layout illustrates space for all users but includes lockers for generally ambulant users. A suitable number of lockers must comply with the requirements of BS8300/ADM for wheelchair users depending upon the expected user group. The following items may be provided: - cube lockers for personal belongings will be required if staff are not allocated their own changing lockers; - shaver sockets, shelves and lights associated with mirrors.
| ADB | [7 empty] | Room Environmental Data
V0554-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0554-03 |  |  |  |  | Staff communal changing room: 30 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0554-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0554-03 |  |  |  |  | Staff communal changing room: 30 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0554-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0554-03 |  |  |  |  | Staff communal changing room: 30 lockers
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 4 |  |  | 4 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | CHA383 |  | CHAIR, stacking, polypropylene, with back and seat pads, wipeable. | [16 empty] | 3
| 30 |  |  | 30 |  |  |  |  | LOC005 |  | LOCKER clothes, single, 1800H 300W 550D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | RAC154 |  | RACK shoe, (bridge unit base between lockers assembly) 175H 1200W 450D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | RAI023 |  | RAIL, coat hanging, 20 secure hangers with sleeve lock chain, (bridge unit top between lockers assembly), 1200W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Semi-ambulant person may undress/dress in privacy. 2) Hanging outdoor clothing. 3) Call systems may be used.
| Personnel: | [6 empty] | 1 x person. Intermittent use.
| Planning Relationships: | [5 empty] | Adjacent to sub-waiting area (if provided). Close to WC facilities. May be use in conjunction with staff changing area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items are shown on the room layout but are optional: - patient/staff call (although required when for patient use); The following items may be provided: - a tip-up seat
| ADB | [7 empty] | Room Environmental Data
V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL006 |  | PULL CORD, patient/staff call (help) with reassurance lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SEA004 |  | SEAT, bench, wall mounted, 480H 1300W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0726-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0726-01 |  |  |  |  | Changing room: independent wheelchair: pass-through
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Wheelchair user may undress/dress independently in privacy. 2) Hanging clothing whilst seated. 3) Call systems may be used. 4) Semi-ambulant person may undress/dress in privacy.
| Personnel: | [6 empty] | 1 x person. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items may be provided: - a bench (instead of the tip-up seat shown on the room layout).
| ADB | [7 empty] | Room Environmental Data
V0726-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0726-01 |  |  |  |  | Changing room: independent wheelchair: pass-through
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0726-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0726-01 |  |  |  |  | Changing room: independent wheelchair: pass-through
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0726-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0726-01 |  |  |  |  | Changing room: independent wheelchair: pass-through
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL006 |  | PULL CORD, patient/staff call (help) with reassurance lamp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | RAI161 |  | RAIL, grab, horizontal, wall or door mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI172 |  | RAIL, grab, hinged, wall mounted, 650mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SEA022 |  | SEAT, tip-up, fixed height | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0922
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0922 |  |  |  |  | WC: independent wheelchair
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Independent wheelchair accessible toilet and adjacent hand-rinse basin may be used. 2) Call systems may be used.
| Personnel: | [6 empty] | 1 x person. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 4.5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items are shown on the drawing but are optional: - the bin for the disposal of sanitary towels is only required in female WCs;
| ADB | [7 empty] | Room Environmental Data
V0922
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0922 |  |  |  |  | WC: independent wheelchair
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 20
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0922
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0922 |  |  |  |  | WC: independent wheelchair
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0922
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0922 |  |  |  |  | WC: independent wheelchair
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAC002 |  | BACKREST, WC/toilet, padded, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL006 |  | PULL CORD, patient/staff call (help) with reassurance lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CIS005 |  | CISTERN WC/toilet, concealed, reversible. To suit WC | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | RAI048 |  | RAIL, grab, vertical, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI159 |  | RAIL, grab, horizontal, with supports, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI161 |  | RAIL, grab, horizontal, wall or door mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI172 |  | RAIL, grab, hinged, wall mounted, 650mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WCH005 |  | WC/toilet pan with seat, 700 mm projection, hospital pattern, rimless pan, vitreous china. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS015 |  | DISPENSER, toilet paper, dispense individual sheets, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE100 |  | SHELF, raised edge, non-breakable, 600W 200D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE102 |  | SHELF, raised edge, non-breakable, 200W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | VEN003 |  | VENDING MACHINE, sanitary towel with coin slot | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN028 |  | BIN, disposal, sealed, operated with one hand, nominal 420H 155W 490D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL003 |  | HOLDER, sack, small, freestanding | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0923
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0923 |  |  |  |  | WC: independent wheelchair/semi-ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Independent wheelchair accessible toilet and adjacent hand-rinse basin may be used. 2) Call systems may be used. 3) Toilet may be used by semi-ambulant person. 4) Hand-rinse basin may be used.
| Personnel: | [6 empty] | 1 x person. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 5.5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The hand-wash basin is only suitable for ambulant and semi-ambulant users. The call repeat lamp is situated over the door outside the room. The following items are shown on the drawing but are optional: - the bin for the disposal of sanitary towels is only required in female WCs; -sanitary dispenser; - mirror, light and shaver outlet.
| ADB | [7 empty] | Room Environmental Data
V0923
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0923 |  |  |  |  | WC: independent wheelchair/semi-ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 20
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0923
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0923 |  |  |  |  | WC: independent wheelchair/semi-ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0923
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V0923 |  |  |  |  | WC: independent wheelchair/semi-ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAC002 |  | BACKREST, WC/toilet, padded, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BAS107 |  | BASIN, medium, general pattern, vitreous china, 2 tap holes, no overflow, bottom outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL006 |  | PULL CORD, patient/staff call (help) with reassurance lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CIS005 |  | CISTERN WC/toilet, concealed, reversible. To suit WC | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG063 |  | LUMINAIRE, single fluorescent lamp, wall, 8 watt, 300 mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR002 |  | MIRROR, wall mounted, 900H 300W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT025 |  | SOCKET outlet, shaver | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | RAI048 |  | RAIL, grab, vertical, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI159 |  | RAIL, grab, horizontal, with supports, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI161 |  | RAIL, grab, horizontal, wall or door mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI172 |  | RAIL, grab, hinged, wall mounted, 650mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP347 |  | TAP, pillar, short lever, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WCH005 |  | WC/toilet pan with seat, 700 mm projection, hospital pattern, rimless pan, vitreous china. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS015 |  | DISPENSER, toilet paper, dispense individual sheets, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE100 |  | SHELF, raised edge, non-breakable, 600W 200D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE102 |  | SHELF, raised edge, non-breakable, 200W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | VEN003 |  | VENDING MACHINE, sanitary towel with coin slot | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN028 |  | BIN, disposal, sealed, operated with one hand, nominal 420H 155W 490D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL003 |  | HOLDER, sack, small, freestanding | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Toilet may be used by ambulant person. 2) Hand-rinse basin may be used.
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following items are shown on the drawing but are optional: - the bin for the disposal of sanitary towels is only required in female WCs; - the shelf next to the basin.
| ADB | [7 empty] | Room Environmental Data
V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 20
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CIS005 |  | CISTERN WC/toilet, concealed, reversible. To suit WC | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WCH001 |  | WC/toilet pan with seat, 520-550 projection, hospital pattern, rimless pan, vitreous china. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL016 |  | HOLDER, toilet roll, multi, large | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN028 |  | BIN, disposal, sealed, operated with one hand, nominal 420H 155W 490D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL004 |  | HOLDER, sack, with lid foot operated, small, freestanding | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V1121
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V1121 |  |  |  |  | WC: semi-ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Toilet may be used by semi-ambulant person. 2) Hand-rinse basin may be used. 3) Call systems may be used.
| Personnel: | [6 empty] | 1 x person. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2.5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items are shown on the drawing but are optional: - the bin for the disposal of sanitary towels is only required in female WCs; - the shelf next to the basin. The following items may be provided: - mirror.
| ADB | [7 empty] | Room Environmental Data
V1121
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V1121 |  |  |  |  | WC: semi-ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 20
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V1121
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V1121 |  |  |  |  | WC: semi-ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V1121
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V1121 |  |  |  |  | WC: semi-ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL006 |  | PULL CORD, patient/staff call (help) with reassurance lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CIS005 |  | CISTERN WC/toilet, concealed, reversible. To suit WC | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR001 |  | MIRROR, wall mounted, 650H 300W | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | RAI048 |  | RAIL, grab, vertical, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI158 |  | RAIL, grab, horizontal, wall / door mounted, 500mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI161 |  | RAIL, grab, horizontal, wall or door mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI172 |  | RAIL, grab, hinged, wall mounted, 650mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WCH001 |  | WC/toilet pan with seat, 520-550 projection, hospital pattern, rimless pan, vitreous china. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS015 |  | DISPENSER, toilet paper, dispense individual sheets, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN028 |  | BIN, disposal, sealed, operated with one hand, nominal 420H 155W 490D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL004 |  | HOLDER, sack, with lid foot operated, small, freestanding | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V1131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V1131 |  |  |  |  | Nappy changing room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Changing nappies. 2) Clinical waste may be disposed 3) Wash-hand basin may be used.
| Personnel: | [6 empty] | 1 x baby or infant. 1 x adult (ambulant).
| Planning Relationships: | [5 empty] | Adjacent to waiting area and/or concourse
| Space Data: | [6 empty] | Area (m²): |  |  |  | 5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The room includes a wall-mounted fold-down changing table, alternatively, it can accommodate a fixed or mobile table. The layout is suitable for ambulant and semi-ambulant users, where access is required for wheelchair users, consideration must be given to the space within the room and fixing height of the changing table.
| ADB | [7 empty] | Room Environmental Data
V1131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V1131 |  |  |  |  | Nappy changing room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V1131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V1131 |  |  |  |  | Nappy changing room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V1131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V1131 |  |  |  |  | Nappy changing room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS107 |  | BASIN, medium, general pattern, vitreous china, 2 tap holes, no overflow, bottom outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | NCU001 |  | BABY NAPPY CHANGING UNIT, folds up base, heavy duty plastic, safety straps, wall mounted, 900H 560W 885D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA383 |  | CHAIR, stacking, polypropylene, with back and seat pads, wipeable. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL008 |  | HOLDER, sack with lid foot operated, large, freestanding, 960H 500W 415D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Shower may be used by ambulant person. 2) User may undress and dress in privacy. 3) Hanging outdoor clothing. 4) Hanging clothes and towels.
| Personnel: | [6 empty] | 1 x person (staff or visitor). Intermittent use.
| Planning Relationships: | [5 empty] | Associated with staff changing area. Close to a WC.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2.5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | This room is not recommended for patient use. The following items may be provided: - inward opening door; - full length mirror.
| ADB | [7 empty] | Room Environmental Data
V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 100-150
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | DIS200 |  | DISH, soap, wall mounted | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG063 |  | LUMINAIRE, single fluorescent lamp, wall, 8 watt, 300 mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR002 |  | MIRROR, wall mounted, 900H 300W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT025 |  | SOCKET outlet, shaver | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI260 |  | RAIL for shower curtain, 1000mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SEA024 |  | SEAT, tip-up, wall mounted, 400 W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO009 |  | SHOWER TRAY ceramic slip resistant base, with drainage outlet, 800W 800D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO018 |  | SHOWER, valve, thermostatic mixer (associated with SHO020). | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO020 |  | SHOWER, adjustable shower head hand spray (associated with SHO018). | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC014 |  | SWITCH 5amp ac single pole, 1 way, ceiling pull cord | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W0131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W0131 |  |  |  |  | Store: equipment: local to theatre
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Storage of operating table accessories and items in frequent use. 2) Anaesthetic accessories and equipment are stored.
Personnel:
| Planning Relationships: | [5 empty] | Easy access to associated theatre.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 1 |  |  |  |  | Height (mm): |  |  |  | 2400
Notes:
| ADB | [7 empty] | Room Environmental Data
W0131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W0131 |  |  |  |  | Store: equipment: local to theatre
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W0131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W0131 |  |  |  |  | Store: equipment: local to theatre
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W0131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W0131 |  |  |  |  | Store: equipment: local to theatre
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | HOO020 |  | HOOK, single, large, wall mounted | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SHE231 |  | SHELF, 1500W 300D | [16 empty] | 1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W0625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W0625 |  |  |  |  | Scrub suit supply
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Protective scrub wear will be held/stored/exchanged.
| Personnel: | [6 empty] | Intermittent use.
| Planning Relationships: | [5 empty] | Convenient to locker rooms.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 4 |  |  |  |  | Height (mm): |  |  |  | 2400
Notes:
| ADB | [7 empty] | Room Environmental Data
W0625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W0625 |  |  |  |  | Scrub suit supply
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W0625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W0625 |  |  |  |  | Scrub suit supply
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W0625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W0625 |  |  |  |  | Scrub suit supply
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | RAC379 |  | RACK, stainless steel, 4 wire shelves shelves, 1590H 1220W 455D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W0652
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W0652 |  |  |  |  | Blood refrigerator bay
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Blood and blood products are stored safely and securely. 2) Holding/storing of "out of hours" cross-matched blood.
| Personnel: | [6 empty] | Intermittent use.
| Planning Relationships: | [5 empty] | When defining a location, consideration must be given both to access from clinical spaces for providing supplies and from outside the unit for topping up supplies.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
W0652
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W0652 |  |  |  |  | Blood refrigerator bay
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W0652
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W0652 |  |  |  |  | Blood refrigerator bay
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W0652
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W0652 |  |  |  |  | Blood refrigerator bay
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT058 |  | CONNECTION UNIT switched 13amp, indicating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT059 |  | CONNECTION UNIT switched 13amp, flex, indicator light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | REF080 |  | REFRIGERATOR, blood, 25 packs per drawer, 2 drawer, with built-in alarm system, external temperature gauge, 1030H 690W 760D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SCN001 |  | SCANNER: Bar-code | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W1402
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1402 |  |  |  |  | Store: patients clothing and personal effects
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Security of clothing and personal effects.
| Personnel: | [6 empty] | 1 x Staff Intermittent use
| Planning Relationships: | [5 empty] | This can be a sub-section of another store.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 10 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | Choice of activity unit selection subject to project team decision in order to respond to the operational system chosen.
| ADB | [7 empty] | Room Environmental Data
W1402
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1402 |  |  |  |  | Store: patients clothing and personal effects
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200/300 |  | Subject to perception of detail required
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W1402
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1402 |  |  |  |  | Store: patients clothing and personal effects
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm) In Mental Health accommodation doorsets, including ironmongery, should comply with the requirements set out in "Adult acute mental health units – Planning and design manual Version:0.4:England"
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W1402
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1402 |  |  |  |  | Store: patients clothing and personal effects
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 6 |  |  | 6 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SMF013 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 665D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W1440-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1440-01 |  |  |  |  | Store: bulk clinical supplies
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of all supplies for use within the unit. 2) Bulk supplies are stored. 3) Medical and surgical supplies are stored. 4) Infusion fluids are stored. 5) Bulk packs of disposable bedpans and urine bottles are stored. 6) Equipment trolley(s) may be parked and/or stored. 7) Manoeuvring hand trucks, trolleys and mobile racks. 8) Bar coded items may be tracked.
| Personnel: | [6 empty] | 3 x Staff
| Planning Relationships: | [5 empty] | Near to unit entrance.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 40 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Bulk storage of all supplies, sub-divided as follows: a. sterile items: Instrument trays/packs Sterile consumable items Linen/gowns packs Utensils Gloves etc b. Non-sterile items: Surgical sundries, paper Lotions, pharmaceuticals supplies & intravenous fluids (excluding controlled drugs & drugs liable to misuse.) Laboratory specimen containers. Clean disposable or non-disposable bedpans, urine bottles & vomit bowls. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
W1440-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1440-01 |  |  |  |  | Store: bulk clinical supplies
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 16 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | +ve & -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200/300 |  | Subject to perception of detail required
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W1440-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1440-01 |  |  |  |  | Store: bulk clinical supplies
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W1440-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1440-01 |  |  |  |  | Store: bulk clinical supplies
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT059 |  | CONNECTION UNIT switched 13amp, flex, indicator light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 18 |  |  | 18 |  |  |  |  | SMC051 |  | CABINET, tall, modular storage, for 600 facing inserts, open, on plinth, 2100H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SCN001 |  | SCANNER: Bar-code | [16 empty] | 2
| 8 |  |  | 8 |  |  |  |  | SMF011 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 465D | [16 empty] | 2
| 8 |  |  | 8 |  |  |  |  | SMF013 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 665D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | STO008 |  | STOOL, kick, retractable castors | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W1440-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1440-02 |  |  |  |  | Store: bulk clinical supplies
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of all supplies for use within the unit. 2) Bulk supplies are stored. 3) Medical and surgical supplies are stored. 4) Storing intravenous fluids. 5) Bulk packs of disposable bedpans and urine bottles are stored. 6) Equipment trolley(s) may be parked and/or stored. 7) Moving/manoeuvring trolley(s). 8) Bar coded items may be tracked.
| Personnel: | [6 empty] | 4 x Staff
| Planning Relationships: | [5 empty] | Near to unit entrance.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 80 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Bulk storage of all supplies, sub-divided as follows: a. sterile items: Instrument trays/packs Sterile consumable items Linen/gowns packs Utensils Gloves etc b. Non-sterile items: Surgical sundries, paper Lotions, pharmaceuticals supplies & intravenous fluids (excluding controlled drugs & drugs liable to misuse.) Laboratory specimen containers. Clean disposable or non-disposable bedpans, urine bottles & vomit bowls. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
W1440-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1440-02 |  |  |  |  | Store: bulk clinical supplies
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 16 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | +ve & -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200/300 |  | Subject to perception of detail required
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W1440-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1440-02 |  |  |  |  | Store: bulk clinical supplies
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W1440-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1440-02 |  |  |  |  | Store: bulk clinical supplies
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT059 |  | CONNECTION UNIT switched 13amp, flex, indicator light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 28 |  |  | 28 |  |  |  |  | SMC051 |  | CABINET, tall, modular storage, for 600 facing inserts, open, on plinth, 2100H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SCN001 |  | SCANNER: Bar-code | [16 empty] | 2
| 18 |  |  | 18 |  |  |  |  | SMF011 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 465D | [16 empty] | 2
| 15 |  |  | 15 |  |  |  |  | SMF013 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 665D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | STO008 |  | STOOL, kick, retractable castors | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W1584-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1584-03 |  |  |  |  | Store: clinical equipment
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Medical equipment is stored. 2) Large items of equipment are stored. 3) Mobile equipment may be parked and stored and/or recharged. 4) Equipment is placed on charge.
| Personnel: | [6 empty] | 1-2 x staff. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 32 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | This store includes a mixture of shelving and racking for small equipment and floor space for large equipment.
| ADB | [7 empty] | Room Environmental Data
W1584-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1584-03 |  |  |  |  | Store: clinical equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200/300 |  | Subject to perception of detail required
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W1584-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1584-03 |  |  |  |  | Store: clinical equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W1584-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1584-03 |  |  |  |  | Store: clinical equipment
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 32 |  |  | 32 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PEG005 |  | PEGS, equipment, 3 (500mm spacing), wall mounted | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | SHE253 |  | SHELF, 2100W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | CLI017 |  | CLIP, spring, 32mm dia. 3, mounted on a wooden batten, wall mounted | [16 empty] | 2
| 4 |  |  | 4 |  |  |  |  | SMF011 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 465D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | STO008 |  | STOOL, kick, retractable castors | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W1590
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1590 |  |  |  |  | Store: ready to use medical gas cylinders
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Medical gas cylinders of various sizes are stored by group and type, empty separated from full. 2) Cylinders are prepared for use or disposal. 3) Loading and unloading cylinder trolleys. 4) Statutory notices. may be displayed
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | On outside wall for natural ventilation.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 4 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | Fire equipment and electrical equipment to be in accordance with BS5345 part 1. Natural ventilation grilles required on external wall. Horizontal storage may be required for smaller cylinders C, CD, D and E size. The design should allow for segregation of full and empty cylinders and permit separation of different gases within the store.
| ADB | [7 empty] | Room Environmental Data
W1590
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1590 |  |  |  |  | Store: ready to use medical gas cylinders
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 16 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 16
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200/300 |  | Subject to perception of detail required
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | intrinsically safe lighting
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Intrinsically safe, considre ionisation detector
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W1590
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1590 |  |  |  |  | Store: ready to use medical gas cylinders
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W1590
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1590 |  |  |  |  | Store: ready to use medical gas cylinders
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 4 |  |  | 4 |  |  |  |  | RAC069 |  | RACK, medical gas, 6 cylinder, 1 metre height | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO070 |  | TROLLEY, for single cylinder, type F or G, 1155H 510W 405D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W1594-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1594-01 |  |  |  |  | Store: linen
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Linen and/or towels are stored. 2) Bedding, blankets and pillows are stored. 3) Holding exchange trolley.
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 3 |  |  |  |  | Height (mm): |  |  |  | 2400
Notes:
| ADB | [7 empty] | Room Environmental Data
W1594-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1594-01 |  |  |  |  | Store: linen
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W1594-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1594-01 |  |  |  |  | Store: linen
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W1594-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | W1594-01 |  |  |  |  | Store: linen
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRO233 |  | TROLLEY, clean linen exchange, 3 adjustable shelves, large, 1600H 1600W 680D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0331
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0331 |  |  |  |  | Dirty utility room: bedpan processing
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Disposal of liquid waste. 2) Disposal of bedpans, urine bottles and vomit bowls with contents. 3) Cleansing bedpan holders. 4) Holding/storing working supplies of disposable bedpans, urine bottles and vomit bowls. 5) Holding SHARPS in a container. 6) Items requiring disposal or reprocessing may be held/stored. 7) Holding dirty linen. 8) Sani-chairs and commodes may be parked and/or stored. 9) Clinical wash-hand basin may be used. 10) Urine specimens may be tested. 11) Clinical waste may be disposed 12) Disposal of waste and contaminated materials. 13) Disposal of used protective clothing. 14) Disposal of non-clinical waste.
| Personnel: | [6 empty] | 2 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Close to clinical area, particularly treatment rooms.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The following items may be provided: - placenta weighing scales.
| ADB | [7 empty] | Room Environmental Data
Y0331
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0331 |  |  |  |  | Dirty utility room: bedpan processing
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0331
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0331 |  |  |  |  | Dirty utility room: bedpan processing
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0331
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0331 |  |  |  |  | Dirty utility room: bedpan processing
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU001 |  | DISPOSAL UNIT (macerator), disposable bedpan, bedpan liners/urine bottles, 525W 650D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU006 |  | DISPOSAL UNIT, plain top, right hand drainer, with sink and hopper with flushing rim, 110mm outlet, no tap holes no overflow, back inlet, stainless steel, 1600W 600D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT079 |  | OUTLET isolator, equipment manufacturer's specification | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT301 |  | OUTLET, cold water for equipment | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC023 |  | CABINET, upper, modular storage, for 400 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW052 |  | WORKTOP, clinical, for 2 x 400 facing modular storage cabinets, 910W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS004 |  | DISPENSER, disposable bedpans, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS005 |  | DISPENSER, disposable urine bottles, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS007 |  | DISPENSER, paper towel roll, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS442 |  | DISPENSER, vomit bowls, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | RAC001 |  | RACK, drainage, bedpan holder (5), with drip tray, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CHA338 |  | SANI-CHAIR/COMMODE, tubular, metal, wipeable, mobile. | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0431
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0431 |  |  |  |  | Dirty utility room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Disposal of liquid waste. 2) Holding SHARPS in a container. 3) Items requiring disposal or reprocessing may be held/stored. 4) Clinical wash-hand basin may be used. 5) Urine specimens may be tested. 6) Clinical waste may be disposed 7) Disposal of waste and contaminated materials. 8) Disposal of used protective clothing. 9) Disposal of non-clinical waste.
| Personnel: | [6 empty] | 2 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Close to clinical area, particularly treatment rooms.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
Y0431
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0431 |  |  |  |  | Dirty utility room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0431
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0431 |  |  |  |  | Dirty utility room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0431
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0431 |  |  |  |  | Dirty utility room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU006 |  | DISPOSAL UNIT, plain top, right hand drainer, with sink and hopper with flushing rim, 110mm outlet, no tap holes no overflow, back inlet, stainless steel, 1600W 600D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC023 |  | CABINET, upper, modular storage, for 400 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW052 |  | WORKTOP, clinical, for 2 x 400 facing modular storage cabinets, 910W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS007 |  | DISPENSER, paper towel roll, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 4 |  |  | 4 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0436
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0436 |  |  |  |  | Dirty utility room: theatre
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Disposal of liquid waste. 2) Holding SHARPS in a container. 3) Items requiring disposal or reprocessing may be held/stored. 4) SSD returns trolley is parked/stored. 5) Clinical wash-hand basin may be used. 6) Clinical waste may be disposed 7) Disposal of used protective clothing. 8) Disposal of non-clinical waste. 9) Emptying buckets, etc. 10) Disposal of used packaging materials.
| Personnel: | [6 empty] | 2 x Staff.
| Planning Relationships: | [5 empty] | Direct access from theatre and corridor.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
Y0436
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0436 |  |  |  |  | Dirty utility room: theatre
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | >20
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | n/a
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0436
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0436 |  |  |  |  | Dirty utility room: theatre
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0436
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0436 |  |  |  |  | Dirty utility room: theatre
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU006 |  | DISPOSAL UNIT, plain top, right hand drainer, with sink and hopper with flushing rim, 110mm outlet, no tap holes no overflow, back inlet, stainless steel, 1600W 600D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE211 |  | SHELF, 900W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC023 |  | CABINET, upper, modular storage, for 400 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW052 |  | WORKTOP, clinical, for 2 x 400 facing modular storage cabinets, 910W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLI017 |  | CLIP, spring, 32mm dia. 3, mounted on a wooden batten, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS007 |  | DISPENSER, paper towel roll, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL014 |  | HOLDER, sack, with lid foot operated, large, capacity 120 litre, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL020 |  | HOLDER, sharps box, up to 7 litre capacity, rail/trolley hang or wall mounted, 170H 125W 100D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO024 |  | TROLLEY cleaners, bucket, disposable mop head | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO207 |  | TROLLEY SSD return, 2 door, nominal 970H 1140W 725D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0511
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0511 |  |  |  |  | Utility: footwear washing
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Cleaning footwear in machine.
| Personnel: | [6 empty] | 1 person intermittently
| Planning Relationships: | [5 empty] | Close to staff changing facilities within theatres or catheter laboratories
| Space Data: | [6 empty] | Area (m²): |  |  |  | 4 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
Y0511
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0511 |  |  |  |  | Utility: footwear washing
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0511
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0511 |  |  |  |  | Utility: footwear washing
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0511
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0511 |  |  |  |  | Utility: footwear washing
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | COC001 |  | STOP COCK/PLUG VALVE, ball-o-fix | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT341 |  | OUTLET, drainage, anti-syphon | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW066 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 600W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAS037 |  | WASHING MACHINE, footwear, 850H 900W 660D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0646
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0646 |  |  |  |  | Disposal hold: 3000 litres
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Holding domestic, clinical and recyclable waste for disposal or reprocessing
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Adjacent to main circulation route.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
Ceiling height must allow bin lids to open fully.
| Notes: | [7 empty] | Separate bins/areas must be provided for: - clinical waste; - domestic waste; - recyclable items; - linen; - equipment requiring reprocessing.
| ADB | [7 empty] | Room Environmental Data
Y0646
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0646 |  |  |  |  | Disposal hold: 3000 litres
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0646
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0646 |  |  |  |  | Disposal hold: 3000 litres
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0646
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y0646 |  |  |  |  | Disposal hold: 3000 litres
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BIN037 |  | BIN wheelie, 770 litre, 1360H1360W 800D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Disposal of liquid waste. 2) Filling and emptying cleaning equipment and containers. 3) Holding/storing cleaning equipment. 4) Cleaning equipment may be parked and/or stored. 5) Hand-rinse basin may be used. 6) Sink may be used. 7) Janitorial unit may be used.
| Personnel: | [6 empty] | 2 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Close to areas served.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
If large equipment is stored elsewhere, the size of this room can be reduced.
| Notes: | [7 empty] | This room represents a typical traditional cleaners' room with space for storing a vacuum cleaner, scrubbing/polishing machine (for hard floors) and mop and bucket (stored on the cleaners' trolley). It includes a combined bucket sink and hand-rinse basin (janitorial unit) and separate sink. The following items are shown on the room layout but are optional: - small cube lockers.
| ADB | [7 empty] | Room Environmental Data
Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 22
| Unified Glare Rating Limit (UGRL): | [13 empty] | 80
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Heat
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN10-02 |  |  |  |  | Day surgery facilities
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | HOO020 |  | HOOK, single, large, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE231 |  | SHELF, 1500W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SIN013 |  | SINK and BASIN combination Janitorial unit, hinged bucket grating to sink and monobloc mixer tap with swivel nozzle, stainless steel, 900H 500W 600D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SNU012 |  | SINK UNIT, single bowl with right hand drainer, no tap holes, 1200W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLI017 |  | CLIP, spring, 32mm dia. 3, mounted on a wooden batten, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | LOC012 |  | LOCKER, wall mounted, 340H 300W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLE008 |  | SCRUBBING/POLISHING MACHINE, single brush, 110v machine | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CLE018 |  | CLEANER VACUUM, dry suction, tub, with accessories, filtered air exhaust | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | CON061 |  | CONE, warning, 'wet floor' | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL014 |  | HOLDER, sack, with lid foot operated, large, capacity 120 litre, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAD002 |  | LADDER, 3 tread, platform type 750mm height, folding | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO068 |  | TROLLEY, cleaners, mop bucket, 3 shelves tray and waste sack holder, 980H 1170W 550D | [16 empty] | 3
Activity DataBase
2016-12-29