## Sheet1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | B2425
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | B2425 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Post anaesthetic recovery of patients. 2) Medical and nursing procedures. 3) Observation is undertaken by medical and nursing staff. 4) Clinical wash-hand basin may be used. 5) Mobile equipment and services may be used. 6) Moving/ Manoeuvring beds. 7) Monitoring/diagnostic or therapeutic equipment may be used. 8) Piped medical gases, vacuum and associated equipment may be used.
| Personnel: | [6 empty] | 1 x patient. 1 x staff. 1 x other.
| Planning Relationships: | [5 empty] | Part of multi-bay area. Overall area to include staff communication base and utilities. Close to operating theatre.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 14 |  |  |  |  | Height (mm): |  |  |  | 2700
2700 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | The call repeat lamp is situated outside of the bay. A staff emergency call linked to an emergency call repeat lamp in the staff communications base and each operating theatre required. Note the engineering services included in this data sheet comply with the requirements of HTM 08-03 and superseded the text in para 4.154 of HBN 26-1 and 3.175 of HBN 10-02. For dedicated maternity recovery may only include 1 no. of each s outlet. The following items are shown on the room layout but are optional: - cleaning socket outlet may be shared between multiple bays (9m max cable); - light switch for multiple bay space. The following items may be provided: - when used for maternity provision of a cot(s) may be required; - ceiling-mounted hoist, subject to local policy; - lead protection for mobile imaging, subject to RPA advice. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
B2425
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | B2425 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 500 |  | WP
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
| Standby Lighting Grade - Local Lighting: | [13 empty] | A
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45 |  | The LAmax,f dB noise limit applies only at night 23:00 to 07:00 hours.
| Noise Intrusion (dB) 1hr night: | [13 empty] | 35
| Noise Intrusion (dB) f night: | [13 empty] | 45
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | B2425
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | B2425 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England. All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | B2425
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | B2425 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL035 |  | LAMP repeat call (patient/staff or staff emergency or Cardiac call), ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | IMG002 |  | MONITOR medical display 18"; digital image viewer, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG058 |  | LUMINAIRE, examination, wall, adjustable, 1000 lux | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | RAI130 |  | RAIL, clinical equipment, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRA106 |  | TRACK, curtain, one sided, 4000mm length | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BRA015 |  | BRACKET, flat panel monitor, height adjustable, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL020 |  | HOLDER, sharps box, up to 7 litre capacity, rail/trolley hang or wall mounted, 170H 125W 100D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT002 |  | TROLLEY, modular storage, single open frame, including handle and worktop, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | B2425
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | B2425 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | STO006 |  | STOOL, surgeon/anaesthetist, height adjustable, includes anti-static seat pads | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | B2425-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | B2425-01 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Post anaesthetic recovery of patients. 2) Medical and nursing procedures. 3) Observation is undertaken by medical and nursing staff. 4) Clinical wash-hand basin may be used. 5) Mobile equipment and services may be used. 6) Moving/ Manoeuvring beds. 7) Monitoring/diagnostic or therapeutic equipment may be used. 8) Piped medical gases, vacuum and associated equipment may be used.
| Personnel: | [6 empty] | 1 x patient. 1 x staff. 1 x other.
| Planning Relationships: | [5 empty] | Part of multi-bay area. Overall area to include staff communication base and utilities. Close to operating theatre.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 14 |  |  |  |  | Height (mm): |  |  |  | 2700
2700 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | The call repeat lamp is situated outside of the bay. A staff emergency call linked to an emergency call repeat lamp in the staff communications base and each operating theatre required. Note the engineering services included in this data sheet comply with the requirements of HTM 08-03 and superseded the text in para 4.154 of HBN 26-1 and 3.175 of HBN 10-02. For dedicated maternity recovery may only include 1 no. of each s outlet. The following items are shown on the room layout but are optional: - cleaning socket outlet may be shared between multiple bays (9m max cable); The following items may be provided: - when used for maternity provision of a cot(s) may be required; - ceiling-mounted hoist, subject to local policy; - lead protection for mobile imaging, subject to RPA advice. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
B2425-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | B2425-01 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 500 |  | WP
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
| Standby Lighting Grade - Local Lighting: | [13 empty] | A
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45 |  | The LAmax,f dB noise limit applies only at night 23:00 to 07:00 hours.
| Noise Intrusion (dB) 1hr night: | [13 empty] | 35
| Noise Intrusion (dB) f night: | [13 empty] | 45
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | B2425-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | B2425-01 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England. All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | B2425-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | B2425-01 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL035 |  | LAMP repeat call (patient/staff or staff emergency or Cardiac call), ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | IMG002 |  | MONITOR medical display 18"; digital image viewer, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG058 |  | LUMINAIRE, examination, wall, adjustable, 1000 lux | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | RAI130 |  | RAIL, clinical equipment, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRA180 |  | TRACK, curtain, two sided, L-shape, 3700L 3100W | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BRA015 |  | BRACKET, flat panel monitor, height adjustable, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL020 |  | HOLDER, sharps box, up to 7 litre capacity, rail/trolley hang or wall mounted, 170H 125W 100D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT002 |  | TROLLEY, modular storage, single open frame, including handle and worktop, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | B2425-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | B2425-01 |  |  |  |  | Recovery bay: post anaesthetic
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | STO006 |  | STOOL, surgeon/anaesthetist, height adjustable, includes anti-static seat pads | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | D0434-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | D0434-01 |  |  |  |  | Rest room with beverages & snack preparation bay: 10 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Rest and relaxation or sleeping. 2) Small amounts of dry goods are stored in cupboard(s). 3) Holding/ storing food in refrigerator. 4) Crockery and cutlery are washed mechanically. 5) Hand-rinse basin may be used. 6) Consuming beverages, meals and snacks. 7) People preparing beverages, meals and snacks. 8) Telephone may be used and messages taken. 9) Laptop computer(s) may be used.
| Personnel: | [6 empty] | 10 x persons..
| Planning Relationships: | [5 empty] | Staff use - located away from public areas.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 20.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The following items are shown on the room layout but are optional: - telephone outlet; - mini kitchen water boiler; - mini kitchen microwave. The following items may be provided: - cube lockers for personal belongings; - television, radio - generally not in staff rest areas; - water cooler, or access. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
D0434-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | D0434-01 |  |  |  |  | Rest room with beverages & snack preparation bay: 10 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 – 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V/EM
| Daytime General Service Illuminance (Lux): | [13 empty] | 50 |  | Floor
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 200 |  | On tables
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 300 |  | At servery counter
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | D0434-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | D0434-01 |  |  |  |  | Rest room with beverages & snack preparation bay: 10 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | D0434-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | D0434-01 |  |  |  |  | Rest room with beverages & snack preparation bay: 10 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP715 |  | CUPBOARD, base, including sink panel, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP731 |  | CUPBOARD/DRAWER UNIT, base, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT301 |  | OUTLET, cold water for equipment | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP359 |  | TAP, pillar, high neck, long lever, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAT003 |  | WATER BOILER, 2.5 litre, electric, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WRT221 |  | WORKTOP, dished, stainless steel, with integral centre sink bowl and 2 tap holes, 2100W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP252 |  | CUPBOARD, 2 adjustable shelves, wall mounted, 750H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP259 |  | CUPBOARD, space for built in microwave, wall mounted, 750H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | OVE016 |  | OVEN, microwave, capacity 18 litre, build in, (suitable for CUP259) | [16 empty] | 2
| 8 |  |  | 8 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF058 |  | REFRIGERATOR, capacity 160 litre, automatic defrost, stainless steel, underbench, external temperature gauge, lockable, on castors, 850H 610W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB007 |  | TABLE, 710H 900W 900D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | D0434-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | D0434-02 |  |  |  |  | Rest room with beverages & snack preparation bay: 15 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Rest and relaxation or sleeping. 2) Small amounts of dry goods are stored in cupboard(s). 3) Holding/ storing food in refrigerator. 4) Crockery and cutlery are washed mechanically. 5) Hand-rinse basin may be used. 6) People preparing beverages, meals and snacks. 7) Consuming beverages, meals and snacks. 8) Telephone may be used and messages taken. 9) Laptop computer(s) may be used.
| Personnel: | [6 empty] | 15 x persons..
| Planning Relationships: | [5 empty] | Staff use - located away from public areas.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 28 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The following items are shown on the room layout but are optional: - telephone outlet; - mini kitchen water boiler; - mini kitchen microwave. The following items may be provided: - cube lockers for personal belongings; - television, radio - generally not in staff rest areas; - water cooler, or access. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
D0434-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | D0434-02 |  |  |  |  | Rest room with beverages & snack preparation bay: 15 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 – 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V/EM
| Daytime General Service Illuminance (Lux): | [13 empty] | 50 |  | Floor
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 200 |  | On tables
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 300 |  | At servery counter
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | D0434-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | D0434-02 |  |  |  |  | Rest room with beverages & snack preparation bay: 15 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | D0434-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | D0434-02 |  |  |  |  | Rest room with beverages & snack preparation bay: 15 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP715 |  | CUPBOARD, base, including sink panel, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP731 |  | CUPBOARD/DRAWER UNIT, base, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT301 |  | OUTLET, cold water for equipment | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP359 |  | TAP, pillar, high neck, long lever, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAT003 |  | WATER BOILER, 2.5 litre, electric, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WRT221 |  | WORKTOP, dished, stainless steel, with integral centre sink bowl and 2 tap holes, 2100W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP252 |  | CUPBOARD, 2 adjustable shelves, wall mounted, 750H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP259 |  | CUPBOARD, space for built in microwave, wall mounted, 750H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | OVE016 |  | OVEN, microwave, capacity 18 litre, build in, (suitable for CUP259) | [16 empty] | 2
| 11 |  |  | 11 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF058 |  | REFRIGERATOR, capacity 160 litre, automatic defrost, stainless steel, underbench, external temperature gauge, lockable, on castors, 850H 610W 600D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB135 |  | TABLE, 710H 1500W 900D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | D0434-04
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | D0434-04 |  |  |  |  | Rest room: 30 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Rest and relaxation or sleeping. 2) Laptop computer(s) may be used. 3) Telephone may be used and messages taken.
| Personnel: | [6 empty] | 30 x persons..
| Planning Relationships: | [5 empty] | Staff use - located away from public areas. Easy access to pantry
| Space Data: | [6 empty] | Area (m²): |  |  |  | 45.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The following items may be provided: - cube lockers for personal belongings; - television, radio - generally not in staff rest areas; - water cooler, or access. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
D0434-04
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | D0434-04 |  |  |  |  | Rest room: 30 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 – 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V/EM
| Daytime General Service Illuminance (Lux): | [13 empty] | 50 |  | Floor
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 200 |  | On tables
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | D0434-04
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | D0434-04 |  |  |  |  | Rest room: 30 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | D0434-04
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | D0434-04 |  |  |  |  | Rest room: 30 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 26 |  |  | 26 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 7 |  |  | 7 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB135 |  | TABLE, 710H 1500W 900D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0171
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | G0171 |  |  |  |  | Parking bay: large equipment
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Parking equipment. 2) Equipment is placed on charge.
| Personnel: | [6 empty] | Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 4 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
G0171
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | G0171 |  |  |  |  | Parking bay: large equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | See HVAC notes 2
| Ventilation Type: | [13 empty] | N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
| General Notes: | [5 empty] | Part of corridor space
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0171
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | G0171 |  |  |  |  | Parking bay: large equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0171
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | G0171 |  |  |  |  | Parking bay: large equipment
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0180-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | G0180-01 |  |  |  |  | Parking bay: resusitation trolley
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Mobile equipment may be parked and stored and/or recharged. 2) Equipment is placed on charge. 3) Carrying out routine checks on equipment.
| Personnel: | [6 empty] | Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
G0180-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | G0180-01 |  |  |  |  | Parking bay: resusitation trolley
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | See HVAC notes 2
| Ventilation Type: | [13 empty] | N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
| General Notes: | [5 empty] | Part of corridor space
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0180-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | G0180-01 |  |  |  |  | Parking bay: resusitation trolley
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0180-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | G0180-01 |  |  |  |  | Parking bay: resusitation trolley
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRO310 |  | TROLLEY, emergency/resuscitation, complete with defibrillator, 955H 825W 575D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | H1304-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | H1304-01 |  |  |  |  | Seminar room: 10 places (including 1 wheelchair place)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Seminars/conferences are held. 2) Multimedia equipment may be used. 3) Laptop computer(s) may be used. 4) Telephone(s) may be used.
| Personnel: | [6 empty] | 11 x persons (including lecturer). Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 19.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | For flexibility in use, direct access to a store is required. The call repeat lamp is situated over the door outside the room. The following items may be provided: - a TV; - an overhead projector; - video-conferencing facilities; - an induction loop hearing system; - a public address system (in larger seminar rooms); - a clinical wash-hand basin and gel dispenser to allow for clinical use of the room; - audiovisual links to clinical areas for training purposes; - shelving, desks/tables and computers for training use. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
H1304-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | H1304-01 |  |  |  |  | Seminar room: 10 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 100-150 |  | On floor
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 300 |  | Over working plane
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 52
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 52 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | H1304-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | H1304-01 |  |  |  |  | Seminar room: 10 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control. Blinds will be required to darken room, full blackout is rarely required Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | H1304-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | H1304-01 |  |  |  |  | Seminar room: 10 places (including 1 wheelchair place)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 12 |  |  | 12 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT004 |  | OUTLET cable, fused, 13 amp, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 10 |  |  | 10 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT135 |  | SOCKET outlet, computer data, single, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SCR043 |  | SCREEN, projection, ceiling mounted, 1800H 1800W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA006 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 1200H1800W | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | PRO026 |  | PROJECTOR, multi-media, ceiling mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA051 |  | BOARD, flip chart, height adjustable, freestanding | [16 empty] | 3
| 10 |  |  | 10 |  |  |  |  | CHA318 |  | CHAIR, upright, with arms, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP036 |  | CUPBOARD, steel, 2 adjustable shelves, 2 door, lockable, 900H 900W 420D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB008 |  | TABLE, 710H 1200W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | H1304-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | H1304-02 |  |  |  |  | Seminar room: 20 places (including 1 wheelchair place)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Seminars/conferences are held. 2) Multimedia equipment may be used. 3) Laptop computer(s) may be used. 4) Telephone(s) may be used.
| Personnel: | [6 empty] | 21 x persons (including lecturer). Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 28 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | For flexibility in use, direct access to a store is required. The call repeat lamp is situated over the door outside the room. The following items may be provided: - a TV; - an overhead projector; - video-conferencing facilities; - an induction loop hearing system; - a public address system (in larger seminar rooms); - a clinical wash-hand basin and gel dispenser to allow for clinical use of the room; - audiovisual links to clinical areas for training purposes; - shelving, desks/tables and computers for training use. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
H1304-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | H1304-02 |  |  |  |  | Seminar room: 20 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 100-150 |  | On floor
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 300 |  | Over working plane
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 53
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 53 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | H1304-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | H1304-02 |  |  |  |  | Seminar room: 20 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control. Blinds will be required to darken room, full blackout is rarely required Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | H1304-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | H1304-02 |  |  |  |  | Seminar room: 20 places (including 1 wheelchair place)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 17 |  |  | 17 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT004 |  | OUTLET cable, fused, 13 amp, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 11 |  |  | 11 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT135 |  | SOCKET outlet, computer data, single, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SCR043 |  | SCREEN, projection, ceiling mounted, 1800H 1800W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA006 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 1200H1800W | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | PRO026 |  | PROJECTOR, multi-media, ceiling mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA051 |  | BOARD, flip chart, height adjustable, freestanding | [16 empty] | 3
| 20 |  |  | 20 |  |  |  |  | CHA318 |  | CHAIR, upright, with arms, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP036 |  | CUPBOARD, steel, 2 adjustable shelves, 2 door, lockable, 900H 900W 420D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB008 |  | TABLE, 710H 1200W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | J1264
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | J1264 |  |  |  |  | Waiting bay: 1 patient trolley/bed place
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patients' trolley(s) may be parked or stored. 2) Patient may wait on trolley/bed, under nursing observation.
| Personnel: | [6 empty] | 1 x Patient 1 x Staff
| Planning Relationships: | [5 empty] | Part of sub-waiting area. Integrated with the A&E unit.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 6 |  |  |  |  | Height (mm): |  |  |  | 2400
Height to suit surrounding area.
Notes:
| ADB | [7 empty] | Room Environmental Data
J1264
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | J1264 |  |  |  |  | Waiting bay: 1 patient trolley/bed place
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | -
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 67
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 67 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | J1264
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | J1264 |  |  |  |  | Waiting bay: 1 patient trolley/bed place
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control or Not applicable Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | J1264
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | J1264 |  |  |  |  | Waiting bay: 1 patient trolley/bed place
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRA198 |  | TRACK, curtain, two sided, L-shape, 2100W 3000D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | K0131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | K0131 |  |  |  |  | Pneumatic tube station
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Pneumatic tube may be used. 2) Sending specimens and orders through a pneumatic tube system.
| Personnel: | [6 empty] | Intermittent use
| Planning Relationships: | [5 empty] | The pneumatic tube station is a nominal allocation of space that may be attached to a variety of spaces. When defining a location, consideration must be given both to access from clinical spaces and security of delivered items. The station should be located in a secure area preferably only accessible to staff and which can be locked-if the area is vacated. If a station is to be shared, access arrangements should be agreed and the security of the station assigned to one department.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 1 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
K0131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | K0131 |  |  |  |  | Pneumatic tube station
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | n/a
| Ventilation Type: | [13 empty] | n/a
| Pressure Relative to Adjoining Space: | [13 empty] | n/a
| Supply Air: Final Filter Class | [12 empty] | n/a
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 70
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 70 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | K0131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | K0131 |  |  |  |  | Pneumatic tube station
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | K0131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | K0131 |  |  |  |  | Pneumatic tube station
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | TUB002 |  | TUBE PNEUMATIC System | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1308
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | L1308 |  |  |  |  | Near patient testing room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Electronic patient records (EPRs) may be accessed and updated. 2) Clinical wash-hand basin may be used. 3) Patient records may be reviewed and recorded. 4) Performing electrolyte analysis. 5) Performing blood gas analysis. 6) Performing glucose analysis. 7) Computer workstation(s) may be used. 8) Displaying information. 9) Printer may be used.
| Personnel: | [6 empty] | 2 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | This room is based on the use of an outward opening entrance door, where an entrance door is not provided, the entrance must be within a secure staff area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Type of analyser provided to suit range of tests to be undertaken. The following items are shown on the room layout but are optional: - door to room; - a specimen fridge; - a sink and demineralised water supply. The following items may be provided: - a pneumatic tube to/from pathology. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
L1308
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | L1308 |  |  |  |  | Near patient testing room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1308
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | L1308 |  |  |  |  | Near patient testing room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. Not applicable or 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1308
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | L1308 |  |  |  |  | Near patient testing room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWB080 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 2000W 750D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWS190 |  | WORKTOP, with right hand sink bowl (sink size 200x450x365), 920H 3000W 750D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC023 |  | CABINET, upper, modular storage, for 400 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP022 |  | TAP, laboratory, cold water | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP023 |  | TAP, laboratory, hot water | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | ANA052 |  | ANALYSER, blood gas with electrolytes, 550H 700W 530D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA303 |  | CHAIR, swivel, height adjustable 540-790, tilting back, adjustable footrest, wipeable, 5 star base, on castors/glides | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF060 |  | REFRIGERATOR, reagents, capacity 110 litre, external temperature gauge, automatic defrost, underbench, 850H 500W 590D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SMT001 |  | TROLLEY, modular storage, single open frame, including handle, with up to 5 sets of runners for 600 facing inserts, 850H 730W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Clinical administration. 2) Computer workstation(s) may be used. 3) Telephone(s) may be used. 4) Discussions and interviews may take place. 5) Files and records are stored. 6) Hanging outdoor clothing. 7) Secure holding/storing of clothing and personal belongings. 8) Printer may be used. 9) Electronic patient records (EPRs) may be accessed and updated. 10) Staff notices, information and/or messages may be displayed. 11) Dealing with enquiries. 12) Information on computers may be accessed.
| Personnel: | [6 empty] | 1 x staff Up to x 2 others.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following equipment is shown on the room layout but is optional: - call repeat lamps for controlled drugs cupboards (but required if the office is used for clinical control). The following items may provided; - shelving; - printer. The following items may be provided if the office is used for clinical control: - a small safe; - a key cupboard; - an alarm panel, see HTM 08-03; - a dimming switch - recommended if the room is used for viewing digital images. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 3 |  |  | 3 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG138 |  | LUMINAIRE, indicating controlled drugs cupboard repeat | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB049 |  | CABINET, lateral filing, 6 rails, 2 door, 1970H 1000W 470D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DES026 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1400W 700D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA057 |  | DRAWER UNIT, 3 drawer, lockable, on castors, desk height 715H 430W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0252
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0252 |  |  |  |  | Office: 2 person
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Clinical administration. 2) Computer workstation(s) may be used. 3) Telephone(s) may be used. 4) Discussions and interviews may take place. 5) Files and records are stored. 6) Hanging outdoor clothing. 7) Staff notices, information and/or messages may be displayed. 8) Printer may be used. 9) Dealing with enquiries. 10) Information on computers may be accessed.
| Personnel: | [6 empty] | 2 x staff. Up to 2 x others.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following equipment is shown on the room layout but is optional: - call repeat lamps for controlled drugs cupboards (but required if the office is used for clinical control). The following items may be provided if the office is used for clinical control: - a dimming switch - recommended if the room is used for viewing digital images. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0252
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0252 |  |  |  |  | Office: 2 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0252
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0252 |  |  |  |  | Office: 2 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0252
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0252 |  |  |  |  | Office: 2 person
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 3 |  |  | 3 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG138 |  | LUMINAIRE, indicating controlled drugs cupboard repeat | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB049 |  | CABINET, lateral filing, 6 rails, 2 door, 1970H 1000W 470D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | DES026 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1400W 700D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | DRA057 |  | DRAWER UNIT, 3 drawer, lockable, on castors, desk height 715H 430W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0278-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0278-01 |  |  |  |  | Administration area: shared use: 4 workstations
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Clinical administration. 2) Computer workstation(s) may be used. 3) Telephone(s) may be used. 4) Files and records are stored. 5) Secure holding/storing of clothing and personal belongings.
| Personnel: | [6 empty] | 4 x staff. Up to 2 x others.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 20 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The layout illustrates socket outlets at desk height because they should be easily accessible to enable equipment to be switched off for energy conservation. Floor box services are discouraged as they make it harder to convert the space into a clinical room in the future. It is therefore assumed that the workstations are wire managed. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0278-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0278-01 |  |  |  |  | Administration area: shared use: 4 workstations
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0278-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0278-01 |  |  |  |  | Administration area: shared use: 4 workstations
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0278-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0278-01 |  |  |  |  | Administration area: shared use: 4 workstations
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 4 |  |  | 4 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | DES026 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1400W 700D | [16 empty] | 3
| 12 |  |  | 12 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | DRA057 |  | DRAWER UNIT, 3 drawer, lockable, on castors, desk height 715H 430W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0326-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0326-03 |  |  |  |  | Office: cardiac catheter image review
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Assessment and planning of treatment and/or operation may take place. 2) Computer workstation(s) may be used. 3) Viewing film and/or computer generated images. 4) Telephone(s) may be used.
| Personnel: | [6 empty] | 2 x staff. Up to 6 x others.
| Planning Relationships: | [5 empty] | Accessible to Cardiac Catheter Laboratories
| Space Data: | [6 empty] | Area (m²): |  |  |  | 16 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | A dimming switch is recommended if the room is used for viewing digital images. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0326-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0326-03 |  |  |  |  | Office: cardiac catheter image review
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0326-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0326-03 |  |  |  |  | Office: cardiac catheter image review
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0326-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0326-03 |  |  |  |  | Office: cardiac catheter image review
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 4 |  |  | 4 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WRT054 |  | WORKTOP, non-clinical, 3500W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WRT068 |  | WORKTOP, non-clinical, 1800W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAB027 |  | CABINET, filing, 2 drawer, 710H 800W 470D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB028 |  | TABLE, circular, 710H 900mm dia. | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0727
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0727 |  |  |  |  | Interview room: 7 places (including 1 wheelchair place)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Discussions and interviews may take place. 2) Telephone(s) may be used. 3) Laptop computer(s) may be used. 4) Call systems may be used.
| Personnel: | [6 empty] | Up to 7 x persons.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items are shown on the room layout but are optional: - staff emergency call (not required if the room is for staff use only); - telephone (should not be provided in rooms intended as quiet spaces); - room in use switch and indicator. The following items may be provided: - a clinical wash-hand basin and gel dispenser to allow for clinical use of the room; . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0727
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0727 |  |  |  |  | Interview room: 7 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0727
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0727 |  |  |  |  | Interview room: 7 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0727
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | M0727 |  |  |  |  | Interview room: 7 places (including 1 wheelchair place)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG073 |  | ILLUMINATED SIGN, 'Room in use' | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC076 |  | SWITCH, 'Room in use' illuminated sign. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA311 |  | SOFA CHAIR, 2 seater, easy, with arms, fully upholstered, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | N0112
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0112 |  |  |  |  | Operating theatre: cardiac
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient is transferred from operating table to bed/trolley. 2) Patient is positioned on the operating table. 3) Patient may be connected to anaesthetic machine. 4) Assembling and connecting mobile equipment. 5) Surgical instruments on instrument trolley may be used. 6) Surgical procedures may be performed under local or general anaesthetic. 7) Diagnostic images are viewed on monitor. 8) Used swabs may be checked, weighed and recorded. 9) Operating lists may be displayed. 10) Recording patient data/notes. 11) Maintenance of general anaesthesia. 12) Perfusion (heart/lung) machine is prepared and primed. 13) Imaging x-ray equipment may be used.
| Personnel: | [6 empty] | 1 x patient 8 - 10 x staff
| Planning Relationships: | [5 empty] | Close to Cardiac Catheter laboratories Close to CCU & intensive & intermediate care unit. Access to scrub-up sink or area Access to prep room Close to recovery
| Space Data: | [6 empty] | Area (m²): |  |  |  | 55 |  |  |  |  | Height (mm): |  |  |  | 3000
3000 mm is a nominal height; actual height subject to design, local equipment and environmental considerations.
| Notes: | [7 empty] | "IN USE" sign sited outside the doorway of the room. When laser surgery and X-rays are being undertaken, safety precautions should be employed, including the provision of the warning lights should be located in the corridor above the theatre doors which will be activated prior to laser surgery or X-rays being undertaken. Theatre control panel should be fully recessed and ideally should be accessible for maintenance from outside the theatre. Anaesthetic machine may be located on a dedicated medical supply unit - project team option. All operating lamps should be fitted with provision for a video camera. Connection to the UPS/IPS systems where risk considerations in terms of patient safety dictate. Patient Administration System (PAS) networked to hospital mainframe. Wireways for CCTV to be installed with links to the seminar room and the hospital system as required. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
N0112
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0112 |  |  |  |  | Operating theatre: cardiac
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 25
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | 25 pascals
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 1000
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 500
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 10000 to 100000
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
| Standby Lighting Grade - Local Lighting: | [13 empty] | A
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40 |  | The LAmax,f dB noise limit applies at any time.
| Noise Intrusion (dB) 1hr night: | [13 empty] | 40
| Noise Intrusion (dB) f night: | [13 empty] | 50
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Duct mounted on Supply
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | N0112
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0112 |  |  |  |  | Operating theatre: cardiac
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 4 sets of doors: 2 x personnel & equipment access (1000mm); 1 x personnel, bed, trolley & equipment access (1500mm) 1 x personnel, bed, trolley & equipment access (1900mm)
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control For laser surgery see HBN26 Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | N0112
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0112 |  |  |  |  | Operating theatre: cardiac
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | LIG030 |  | LUMINAIRE, operating theatre, table with two satellite, shadowless, lux 140000 and lux 110000 | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | LIG071 |  | ILLUMINATED SIGN 'RADIATION ON', wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 23 |  |  | 23 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT454 |  | OUTLET, 7 kPa compressed air, surgical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT461 |  | OUTLET, nitrous oxide, medical | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT480 |  | OUTLET, gas scavenging (AGS), medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PAN356 |  | PANEL, control surgical procedure room 900H x 1200W: comprises: 1x Operating lamp ON/OFF switch; 1x Emergency battery lighting"ON"; indicating; 3x General lighting ON/OFF including dimmer switch lamp 1x Standby generator electric mains "ON" indicating lamp; 1x Air temperature indicating gauge 1x Air temperature control 1x Humidity indicating gauge 1x Humidity control and indicating lamp; 1x Ventilation plant "ON"; (NORMAL) indicating lamp 1x Indicating lamp "FILTER REPLACE" 1x Indicating lamp "LOW AIR FLOW"; 1x Indicating lamp "MEDICAL GAS FAILURE" 1x Air sampling grille and duct with temperature and humidity sensors; 1x Clock time elapsed 1x Clock synchronous (time of day) 1x Telephone outlet (splash proof) 1x Room "IN USE"; light, ON/OFF switch 1x Room "IN USE"; light, ON/OFF switch | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PEN040 |  | PENDANT, electrical services and medical gases | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | PEN042 |  | PENDANT, electrical services and medical gases, 2 articulated arms, with docking system, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW069 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 900W 700D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SUC002 |  | SUCTION UNIT, pipeline, high pressure, theatre | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | N0112
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0112 |  |  |  |  | Operating theatre: cardiac
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | ANA004 |  | ANAESTHETIC MACHINE/WORKSTATION with ventilator, with accessories, mobile, 1580H 565W 695D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA324 |  | CHAIR, anaesthetist, wipeable, height adjustable. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CRD012 |  | MACHINE HEART-LUNG BYPASS (perfusion) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CRD016 |  | ECHOCARDIOGRAPHY MACHINE | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DIA003 |  | DIATHERMY APPARATUS, surgical, monopolar and bipolar operation, portable, 190H 400W 330D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DIA006 |  | SMOKE EVACUATION SYSTEM, diathermy, 230H 340W 340D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL014 |  | HOLDER, sack, with lid foot operated, large, capacity 120 litre, mobile | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | INF002 |  | INFUSION volumetric pump, 188H 110W 60D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | KIC001 |  | KICKABOUT, bowl stand, stainless steel, 360mm dia. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC029 |  | MICROSCOPE, surgical, floor standing, 1700H 875W 1880D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | PLA002 |  | PLATFORM, step-stand, stackable, portable, 130H 480W 330D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SCA012 |  | SCALE, swab, includes Mains adaptor | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | STA101 |  | STAND, lotion bowl, single, stainless steel, (Bowls not included) | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | STA102 |  | STAND, 2 lotion bowls, stainless steel, (Bowls not included). | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | STA142 |  | STAND, infusion, twin hook, breaks, mobile | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | STO006 |  | STOOL, surgeon/anaesthetist, height adjustable, includes anti-static seat pads | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | SYR002 |  | SYRINGE pump, battery operated, 366H 127W 80D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB077 |  | TABLE, surgical procedures, radiotranslucen,t o/a 1005H 2100W 835D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRF002 |  | AUTOTRANSFUSION cell separator, mobile, built in air and foam detector, 1620H 270W 585D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO133 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 750W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO140 |  | TROLLEY diathermy equipment, 1 shelf, 870H 490W 650D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | N0112
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0112 |  |  |  |  | Operating theatre: cardiac
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | TRO201 |  | TROLLEY, instruments, stainless steel, buffered, 870H 920W 620D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO204 |  | TROLLEY instrument tray MAYO, 650W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | WAR053 |  | WARMER, blood/fluid, maintains temperature between 36 and 43 deg.C at flow rates up to 500 ml/min, 35H 235W 273D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | N0219
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0219 |  |  |  |  | Scrub-up and gowning bay: 2 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Staff are able to scrub up within sight of clock. 2) Donning a sterile gown and gloves. 3) Dispensing disposable gloves. 4) Holding/storing protective sterile clothing and gloves.
| Personnel: | [6 empty] | Up to 3 staff.
| Planning Relationships: | [5 empty] | The scrub-up and gowning bay is intended as a recess off the treatment room or operating theatre.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 7 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | The following items are shown on the room layout but are optional: - shelving which may be replaced by a supplies trolley with or without a top for opening gowning packs. The following items may be provided: - sterile glove dispenser, assume to be stored on the shelving but may be located in a wall mounted dispenser; - lead apron rack.
| ADB | [7 empty] | Room Environmental Data
N0219
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0219 |  |  |  |  | Scrub-up and gowning bay: 2 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Duct mounted on Supply
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | N0219
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0219 |  |  |  |  | Scrub-up and gowning bay: 2 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. Not applicable or 1 doorset: 1 x personnel access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | N0219
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0219 |  |  |  |  | Scrub-up and gowning bay: 2 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SHE212 |  | SHELF, 900W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRO602 |  | TROUGH scrub-up, hospital pattern, stainless steel, double, 75mm upstand, 950H 1600W 450D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS006 |  | DISPENSER, disposable nailbrush, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | N0226
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0226 |  |  |  |  | Scrub-up and gowning room: 3 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Staff are able to scrub up within sight of clock. 2) Donning sterile gowns and gloves, from a trolley, assisted by a circulating nurse. 3) Donning protective apron and face mask. 4) Dispensing disposable aprons. 5) Holding/storing sterile gown packs for one surgical session with a stock of glove packs and masks. 6) Disposal of pack wrappers and paper towels. 7) Operating lists may be displayed.
| Personnel: | [6 empty] | Up to 4 staff.
| Planning Relationships: | [5 empty] | The scrub-up and gowning room is intended as a recess off the theatres. There is no door between this space and the operating theatre but there may be a direct door from the corridor or preparation subject to space and consideration of safe access.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 11 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | The following items are shown on the room layout but are optional: - shelving which may be replaced by a supplies trolley with or without a top for opening gowning packs. The following items may be provided: - sterile glove dispenser, assume to be stored on the shelving but may be located in a wall mounted dispenser; - lead apron rack.
| ADB | [7 empty] | Room Environmental Data
N0226
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0226 |  |  |  |  | Scrub-up and gowning room: 3 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
Minimum Air Changes (AC/hr):
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | 25 pascals
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Duct mounted on Supply
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | N0226
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0226 |  |  |  |  | Scrub-up and gowning room: 3 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. Not applicable or 1 doorset: 1 x personnel access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | N0226
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0226 |  |  |  |  | Scrub-up and gowning room: 3 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE252 |  | SHELF, 2100W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRO603 |  | TROUGH scrub-up, hospital pattern, stainless steel, triple, 75mm upstand, 950H 2400W 450D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | DIS006 |  | DISPENSER, disposable nailbrush, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | N0317-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0317-01 |  |  |  |  | Anaesthetic room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Anaesthetic accessories and equipment are stored. 2) Controlled and scheduled drugs are stored securely. 3) Holding/storing sterile equipment. 4) Holding/storing stock of infusion fluids. 5) Refrigerated storage of drugs/medicines. 6) Operating lists may be displayed. 7) Recording patient data/notes. 8) Collecting used anaesthetic accessories for reprocessing. 9) Collecting waste materials for disposal. 10) Clinical wash-hand basin may be used. 11) Administration of intravenous analgesia. 12) Maintenance of general anaesthesia. 13) Monitoring/diagnostic or therapeutic equipment may be used.
| Personnel: | [6 empty] | 1 x patient. 4 x staff. 1 x relative accompanying a child patient.
| Planning Relationships: | [5 empty] | Direct access from corridor and into theatre.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 19 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Consideration should be given to the patient transfer methodology (i.e. within anaesthetic room or theatre and where and how hoists are used). The call repeat lamp and controlled drugs cupboard indicator are situated over the door outside the room. The following items are shown on the room layout but are optional: - room in use switch and indicator. The following items may be provided: - a music system may be provided to reduce patient anxiety; - specialist table attachments may be stored here; - ceiling mounted hoist subject to local evaluation of space and fittings. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
N0317-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0317-01 |  |  |  |  | Anaesthetic room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | >10 pascals.
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 1000
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
| Standby Lighting Grade - Local Lighting: | [13 empty] | A
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Duct mounted on Supply
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | N0317-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0317-01 |  |  |  |  | Anaesthetic room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel, bed, trolley, wheelchair & equipment access (personnel, bed, trolley, wheelchair & equipment access (1500mm))
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | N0317-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0317-01 |  |  |  |  | Anaesthetic room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG053 |  | LUMINAIRE, examination, ceiling, adjustable, 1000 lux | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG073 |  | ILLUMINATED SIGN, 'Room in use' | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG138 |  | LUMINAIRE, indicating controlled drugs cupboard repeat | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT004 |  | OUTLET cable, fused, 13 amp, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT050 |  | OUTLET, controlled drugs cupboard | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT056 |  | CONNECTION UNIT, unswitched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT461 |  | OUTLET, nitrous oxide, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT480 |  | OUTLET, gas scavenging (AGS), medical | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SMC023 |  | CABINET, upper, modular storage, for 400 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW090 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 3000W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SUC001 |  | SUCTION UNIT, pipeline, high/low pressure, rail/wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC076 |  | SWITCH, 'Room in use' illuminated sign. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB064 |  | CABINET, metal, controlled drugs, 1 door, lockable, with warning light, wall mounted, 550H 600W 300D | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | N0317-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | N0317-01 |  |  |  |  | Anaesthetic room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | ANA001 |  | ANAESTHETIC MACHINE/WORKSTATION electrically powered piston ventilator, mobile, 1350H 750W 650D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL020 |  | HOLDER, sharps box, up to 7 litre capacity, rail/trolley hang or wall mounted, 170H 125W 100D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF059 |  | REFRIGERATOR, medical (drug/vaccine), capacity 160 litre, external temperature gauge, automatic defrost, lockable, underbench, 850H 550W 620D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STA142 |  | STAND, infusion, twin hook, breaks, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STO006 |  | STOOL, surgeon/anaesthetist, height adjustable, includes anti-static seat pads | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SYR004 |  | SYRINGE pump, anaesthetic use, with diprifusor, 115H 400W 180D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | T0213
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0213 |  |  |  |  | Staff communication base: recovery: 2 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Electronic patient records (EPRs) may be accessed and updated. 2) Computer workstation(s) may be used. 3) Dealing with enquiries. 4) Telephone(s) may be used. 5) Staff supervise and observe patients. 6) Carrying out administration and clerical duties. 7) Information may be provided to patients, carers and visitors. 8) Clinical administration. 9) Clinical hand washing. 10) Operating lists may be displayed. 11) Storing controlled medicines and pharmaceuticals. 12) Non-controlled medicines and pharmaceuticals are stored securely.
| Personnel: | [6 empty] | 2 x staff. 2 x other staff or patients/visitors.
| Planning Relationships: | [5 empty] | Situated to allow easy access and good observation of the recovery area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 13 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | Clear access space around the staff communication base should be maintained even when someone is standing at the front of the base. Consideration should be given to wheelchair access for visitors at staff base. The following items are shown on the room layout but are optional: - controlled drugs cupboard alarm; - call system alarm panel, see HTM 08-03; The following items may be provided: - departmental controlled entry system. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
T0213
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0213 |  |  |  |  | Staff communication base: recovery: 2 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
| Nighttime General Service Illuminance (Lux): | [13 empty] | 30-200
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
| Standby Lighting Grade - Local Lighting: | [13 empty] | A
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | T0213
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0213 |  |  |  |  | Staff communication base: recovery: 2 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | T0213
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0213 |  |  |  |  | Staff communication base: recovery: 2 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | COU138 |  | COUNTER UNIT, 3700W 3000D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT050 |  | OUTLET, controlled drugs cupboard | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT056 |  | CONNECTION UNIT, unswitched, 13 amp | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT151 |  | SOCKET outlet patient monitoring | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PAN063 |  | PANEL, indicator | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | SMC064 |  | CABINET, base, modular storage, for 600 facing inserts, with door, on plinth, 700H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB064 |  | CABINET, metal, controlled drugs, 1 door, lockable, with warning light, wall mounted, 550H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF091 |  | REFRIGERATOR, drug, capacity 35 litre, external temperature gauge, lockable, wall mounted, 510H 380W 445D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | T0213
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0213 |  |  |  |  | Staff communication base: recovery: 2 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | MON110 |  | MONITOR, control central monitoring for recovery orcritical care unit multiparameter monitors up to 16 beds, touch screen, 20" screen | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | T0522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0522 |  |  |  |  | Preparation room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Trays are prepared and trolleys laid up for surgical/clinical procedures. 2) Sterile pre-set trays are held/stored 3) Sterile equipment, consumable supplies and packs are stored. 4) Non-sterile medical items, equipment and supplies are stored. 5) Sterile fluids are stored. 6) Instrument trolleys are held/stored. 7) Storing sundries and small items.
| Personnel: | [6 empty] | 2-3 x staff.
| Planning Relationships: | [5 empty] | Direct access to operating theatre. Access from corridor for delivery of supplies.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The number and size of dressing/instrument trolleys is a project team option. The following items are shown on the room layout but are optional: - heated lotion cabinet which could be provided in a central store instead of within the preparation room. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
T0522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0522 |  |  |  |  | Preparation room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | >25
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | 35 pascals
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40 |  | The LAmax,f dB noise limit applies at any time.
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | 50
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | T0522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0522 |  |  |  |  | Preparation room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control, security control as necessary, see BS2881 Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | T0522
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0522 |  |  |  |  | Preparation room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SMC051 |  | CABINET, tall, modular storage, for 600 facing inserts, open, on plinth, 2100H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW025 |  | WORKTOP, clinical, for 600 facing modular storage cabinets, 1500W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAB036 |  | CABINET warming, lotion, 48x1 litre, 1320H 620W 630D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SMF011 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 465D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STA102 |  | STAND, 2 lotion bowls, stainless steel, (Bowls not included). | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO133 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 750W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO201 |  | TROLLEY, instruments, stainless steel, buffered, 870H 920W 620D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | T0522-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0522-01 |  |  |  |  | Preparation room: shared between theatres
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Trays are prepared and trolleys laid up for surgical/clinical procedures. 2) Sterile pre-set trays are held/stored 3) Sterile equipment, consumable supplies and packs are stored. 4) Non-sterile medical items, equipment and supplies are stored. 5) Sterile fluids are stored. 6) Instrument trolleys are held/stored. 7) Storing sundries and small items.
| Personnel: | [6 empty] | 4 - 5 x staff.
| Planning Relationships: | [5 empty] | Direct access to both operating theatres Access from corridor for delivery of supplies.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 20 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The number and size of dressing/instrument trolleys is a project team option. The following items are shown on the room layout but are optional: - heated lotion cabinet which could be provided in a central store instead of within the preparation room. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
T0522-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0522-01 |  |  |  |  | Preparation room: shared between theatres
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | >10
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | 25 pascals
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40 |  | The LAmax,f dB noise limit applies at any time.
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | 50
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | T0522-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0522-01 |  |  |  |  | Preparation room: shared between theatres
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 3 sets of doors: 3 x personnel, trolley & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control, security control as necessary, see BS2881 Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | T0522-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0522-01 |  |  |  |  | Preparation room: shared between theatres
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 7 |  |  | 7 |  |  |  |  | SMC053 |  | CABINET, tall, modular storage, for 600 facing inserts, with door, on plinth, 2100H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW052 |  | WORKTOP, clinical, for 2 x 400 facing modular storage cabinets, 910W 700D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMW078 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 1800W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAB036 |  | CABINET warming, lotion, 48x1 litre, 1320H 620W 630D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STA102 |  | STAND, 2 lotion bowls, stainless steel, (Bowls not included). | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | TRO133 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 750W 450D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO201 |  | TROLLEY, instruments, stainless steel, buffered, 870H 920W 620D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | T0522-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0522-02 |  |  |  |  | Preparation room: shared between catheter laboratories
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Trays are prepared and trolleys laid up for surgical/clinical procedures. 2) Sterile pre-set trays are held/stored 3) Sterile equipment, consumable supplies and packs are stored. 4) Non-sterile medical items, equipment and supplies are stored. 5) Sterile fluids are stored. 6) Instrument trolleys are held/stored. 7) Storing sundries and small items.
| Personnel: | [6 empty] | 3 - 4 x staff.
| Planning Relationships: | [5 empty] | Direct access to both operating theatres Access from the clean utility room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The number and size of dressing/instrument trolleys is a project team option. The following items may be provided: - heated lotion cabinet which could be provided in a central store instead of within the preparation room. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
T0522-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0522-02 |  |  |  |  | Preparation room: shared between catheter laboratories
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | >25
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | 35 pascals
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40 |  | The LAmax,f dB noise limit applies at any time.
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | 50
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | T0522-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0522-02 |  |  |  |  | Preparation room: shared between catheter laboratories
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 3 sets of doors: 3 x personnel, trolley & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control, security control as necessary, see BS2881 Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | T0522-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0522-02 |  |  |  |  | Preparation room: shared between catheter laboratories
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW052 |  | WORKTOP, clinical, for 2 x 400 facing modular storage cabinets, 910W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW087 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 2700W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STA102 |  | STAND, 2 lotion bowls, stainless steel, (Bowls not included). | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO133 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 750W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO201 |  | TROLLEY, instruments, stainless steel, buffered, 870H 920W 620D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | T0531
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0531 |  |  |  |  | Preparation room: catheter laboratories/enhanced procedures
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Holding/storing working supply of clean and sterile materials for immediate use. 2) Sterile pre-set trays are held/stored 3) A working supply of consumables is held/stored. 4) Operating lists may be displayed. 5) Sterile fluids are stored. 6) Trays are prepared and trolleys laid up for surgical/clinical procedures. 7) Instrument trolleys are held/stored.
| Personnel: | [6 empty] | 1-2 staff intermittently
| Planning Relationships: | [5 empty] | Adjacent to enhanced procedures room. Goods to be delivered from corridor.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 9 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The number and size of dressing/instrument trolleys is a project team option. The following items may be provided: - heated lotion cabinet which could be provided in a central store instead of within the preparation room. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
T0531
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0531 |  |  |  |  | Preparation room: catheter laboratories/enhanced procedures
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40 |  | The LAmax,f dB noise limit applies at any time.
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | 50
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | T0531
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0531 |  |  |  |  | Preparation room: catheter laboratories/enhanced procedures
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control, security control as necessary, see BS2881 Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | T0531
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0531 |  |  |  |  | Preparation room: catheter laboratories/enhanced procedures
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW087 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 2700W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STA102 |  | STAND, 2 lotion bowls, stainless steel, (Bowls not included). | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO133 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 750W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO201 |  | TROLLEY, instruments, stainless steel, buffered, 870H 920W 620D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | T0551
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0551 |  |  |  |  | Workroom: perfusion
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Perfusion (heart/lung) machine is prepared and primed. 2) Equipment and machines may be cleaned and dryed. 3) Medical equipment is stored. 4) Equipment is tested. 5) Statutory notices. may be displayed 6) Equipment is placed on charge. 7) Clinical hand washing. 8) Computer workstation(s) may be used.
| Personnel: | [6 empty] | 1 - 2 x Staff Intermittent use
| Planning Relationships: | [5 empty] | Close to cardiac theatre.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 35 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
T0551
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0551 |  |  |  |  | Workroom: perfusion
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | >25
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | 35 pascals
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | T0551
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0551 |  |  |  |  | Workroom: perfusion
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel, trolley & equipment access (1500mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass, high level Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | T0551
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0551 |  |  |  |  | Workroom: perfusion
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 14 |  |  | 14 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMW078 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 1800W 700D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMW090 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 3000W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 3 |  |  | 3 |  |  |  |  | CHA304 |  | CHAIR, swivel, height adjustable, medium back, wipeable, 5 star base, on glides | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CRD005 |  | PUMP, Intra-Aortic Balloon | [16 empty] | 3
| 5 |  |  | 5 |  |  |  |  | CRD012 |  | MACHINE HEART-LUNG BYPASS (perfusion) | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL014 |  | HOLDER, sack, with lid foot operated, large, capacity 120 litre, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRF002 |  | AUTOTRANSFUSION cell separator, mobile, built in air and foam detector, 1620H 270W 585D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | T0551-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0551-02 |  |  |  |  | Store: perfusion
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Medical equipment is stored. 2) Holding/storing working supplies of disposable items. 3) Statutory notices. may be displayed 4) Clinical hand washing.
| Personnel: | [6 empty] | 1 - 2 x Staff Intermittent use
| Planning Relationships: | [5 empty] | Adjacent to perfusion workroom. Close to cardiac theatre.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 20 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
T0551-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0551-02 |  |  |  |  | Store: perfusion
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | F7
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A
| Standby Lighting Grade - Local Lighting: | [13 empty] | A
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [15 empty] | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | T0551-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0551-02 |  |  |  |  | Store: perfusion
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1500mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass, high level Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | T0551-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | T0551-02 |  |  |  |  | Store: perfusion
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE222 |  | SHELF, 1200W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW075 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 1500W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 5 |  |  | 5 |  |  |  |  | SMF011 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 465D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CRD005 |  | PUMP, Intra-Aortic Balloon | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL014 |  | HOLDER, sack, with lid foot operated, large, capacity 120 litre, mobile | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | PLA005 |  | PLATFORM, storage, slatted, 300H 1200W 800D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | TRF002 |  | AUTOTRANSFUSION cell separator, mobile, built in air and foam detector, 1620H 270W 585D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0554
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V0554 |  |  |  |  | Staff communal changing room: 20 lockers
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) User may undress and dress. 2) Changing into clean uniforms (including blues or greens). 3) Changing footwear. 4) Secure hanging of wet outdoor clothing. 5) Secure holding/storing of clothing and personal belongings. 6) Secure holding/storage of motorcycle and bicycle helmets. 7) Hanging outdoor clothing. 8) Disposal of dirty uniforms.
| Personnel: | [6 empty] | Up to 6 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Direct access to showers and/or individual changing room(s). Close to WCs. Close to uniform exchange, if provided.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 20 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | It is assumed that this space is supported by one individual changing room. See V0725 for details of semi-ambulant individual changing room and V0276 for independent wheelchair individual changing room. The room layout illustrates space for all users but includes lockers for generally ambulant users. A suitable number of lockers must comply with the requirements of BS8300/ADM for wheelchair users depending upon the expected user group. The following items may be provided: - cube lockers for personal belongings will be required if staff are not allocated their own changing lockers; - shaver sockets, shelves and lights associated with mirrors.
| ADB | [7 empty] | Room Environmental Data
V0554
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V0554 |  |  |  |  | Staff communal changing room: 20 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0554
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V0554 |  |  |  |  | Staff communal changing room: 20 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0554
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V0554 |  |  |  |  | Staff communal changing room: 20 lockers
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 3 |  |  | 3 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | CHA383 |  | CHAIR, stacking, polypropylene, with back and seat pads, wipeable. | [16 empty] | 3
| 20 |  |  | 20 |  |  |  |  | LOC005 |  | LOCKER clothes, single, 1800H 300W 550D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC154 |  | RACK shoe, (bridge unit base between lockers assembly) 175H 1200W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAI023 |  | RAIL, coat hanging, 20 secure hangers with sleeve lock chain, (bridge unit top between lockers assembly), 1200W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0554-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V0554-03 |  |  |  |  | Staff communal changing room: 30 lockers
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) User may undress and dress. 2) Changing into clean uniforms (including blues or greens). 3) Changing footwear. 4) Secure hanging of wet outdoor clothing. 5) Secure holding/storing of clothing and personal belongings. 6) Secure holding/storage of motorcycle and bicycle helmets. 7) Hanging outdoor clothing. 8) Disposal of dirty uniforms.
| Personnel: | [6 empty] | Up to 12 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Direct access to showers and/or individual changing room(s). Close to WCs. Close to uniform exchange, if provided.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 30 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | It is assumed that this space is supported by one individual changing room. See V0725 for details of semi-ambulant individual changing room and V0276 for independent wheelchair individual changing room. The room layout illustrates space for all users but includes lockers for generally ambulant users. A suitable number of lockers must comply with the requirements of BS8300/ADM for wheelchair users depending upon the expected user group. The following items may be provided: - cube lockers for personal belongings will be required if staff are not allocated their own changing lockers; - shaver sockets, shelves and lights associated with mirrors.
| ADB | [7 empty] | Room Environmental Data
V0554-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V0554-03 |  |  |  |  | Staff communal changing room: 30 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0554-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V0554-03 |  |  |  |  | Staff communal changing room: 30 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0554-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V0554-03 |  |  |  |  | Staff communal changing room: 30 lockers
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 4 |  |  | 4 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | CHA383 |  | CHAIR, stacking, polypropylene, with back and seat pads, wipeable. | [16 empty] | 3
| 30 |  |  | 30 |  |  |  |  | LOC005 |  | LOCKER clothes, single, 1800H 300W 550D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | RAC154 |  | RACK shoe, (bridge unit base between lockers assembly) 175H 1200W 450D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | RAI023 |  | RAIL, coat hanging, 20 secure hangers with sleeve lock chain, (bridge unit top between lockers assembly), 1200W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Semi-ambulant person may undress/dress in privacy. 2) Hanging outdoor clothing. 3) Call systems may be used.
| Personnel: | [6 empty] | 1 x person. Intermittent use.
| Planning Relationships: | [5 empty] | Adjacent to sub-waiting area (if provided). Close to WC facilities. May be use in conjunction with staff changing area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items are shown on the room layout but are optional: - patient/staff call (although required when for patient use); The following items may be provided: - a tip-up seat
| ADB | [7 empty] | Room Environmental Data
V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL006 |  | PULL CORD, patient/staff call (help) with reassurance lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SEA004 |  | SEAT, bench, wall mounted, 480H 1300W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0922
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V0922 |  |  |  |  | WC: independent wheelchair
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Independent wheelchair accessible toilet and adjacent hand-rinse basin may be used. 2) Call systems may be used.
| Personnel: | [6 empty] | 1 x person. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 4.5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items are shown on the drawing but are optional: - the bin for the disposal of sanitary towels is only required in female WCs;
| ADB | [7 empty] | Room Environmental Data
V0922
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V0922 |  |  |  |  | WC: independent wheelchair
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 20
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0922
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V0922 |  |  |  |  | WC: independent wheelchair
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0922
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V0922 |  |  |  |  | WC: independent wheelchair
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAC002 |  | BACKREST, WC/toilet, padded, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL006 |  | PULL CORD, patient/staff call (help) with reassurance lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CIS005 |  | CISTERN WC/toilet, concealed, reversible. To suit WC | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | RAI048 |  | RAIL, grab, vertical, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI159 |  | RAIL, grab, horizontal, with supports, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI161 |  | RAIL, grab, horizontal, wall or door mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI172 |  | RAIL, grab, hinged, wall mounted, 650mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WCH005 |  | WC/toilet pan with seat, 700 mm projection, hospital pattern, rimless pan, vitreous china. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS015 |  | DISPENSER, toilet paper, dispense individual sheets, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE100 |  | SHELF, raised edge, non-breakable, 600W 200D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE102 |  | SHELF, raised edge, non-breakable, 200W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | VEN003 |  | VENDING MACHINE, sanitary towel with coin slot | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN028 |  | BIN, disposal, sealed, operated with one hand, nominal 420H 155W 490D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL003 |  | HOLDER, sack, small, freestanding | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Toilet may be used by ambulant person. 2) Hand-rinse basin may be used.
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following items are shown on the drawing but are optional: - the bin for the disposal of sanitary towels is only required in female WCs; - the shelf next to the basin.
| ADB | [7 empty] | Room Environmental Data
V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 20
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CIS005 |  | CISTERN WC/toilet, concealed, reversible. To suit WC | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WCH001 |  | WC/toilet pan with seat, 520-550 projection, hospital pattern, rimless pan, vitreous china. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL016 |  | HOLDER, toilet roll, multi, large | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN028 |  | BIN, disposal, sealed, operated with one hand, nominal 420H 155W 490D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL004 |  | HOLDER, sack, with lid foot operated, small, freestanding | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Shower may be used by ambulant person. 2) User may undress and dress in privacy. 3) Hanging outdoor clothing. 4) Hanging clothes and towels.
| Personnel: | [6 empty] | 1 x person (staff or visitor). Intermittent use.
| Planning Relationships: | [5 empty] | Associated with staff changing area. Close to a WC.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2.5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | This room is not recommended for patient use. The following items may be provided: - inward opening door; - full length mirror.
| ADB | [7 empty] | Room Environmental Data
V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 100-150
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | DIS200 |  | DISH, soap, wall mounted | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG063 |  | LUMINAIRE, single fluorescent lamp, wall, 8 watt, 300 mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR002 |  | MIRROR, wall mounted, 900H 300W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT025 |  | SOCKET outlet, shaver | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI260 |  | RAIL for shower curtain, 1000mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SEA024 |  | SEAT, tip-up, wall mounted, 400 W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO009 |  | SHOWER TRAY ceramic slip resistant base, with drainage outlet, 800W 800D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO018 |  | SHOWER, valve, thermostatic mixer (associated with SHO020). | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO020 |  | SHOWER, adjustable shower head hand spray (associated with SHO018). | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC014 |  | SWITCH 5amp ac single pole, 1 way, ceiling pull cord | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W0652
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | W0652 |  |  |  |  | Blood refrigerator bay
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Blood and blood products are stored safely and securely. 2) Holding/storing of "out of hours" cross-matched blood.
| Personnel: | [6 empty] | Intermittent use.
| Planning Relationships: | [5 empty] | When defining a location, consideration must be given both to access from clinical spaces for providing supplies and from outside the unit for topping up supplies.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
W0652
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | W0652 |  |  |  |  | Blood refrigerator bay
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W0652
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | W0652 |  |  |  |  | Blood refrigerator bay
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W0652
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | W0652 |  |  |  |  | Blood refrigerator bay
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT058 |  | CONNECTION UNIT switched 13amp, indicating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT059 |  | CONNECTION UNIT switched 13amp, flex, indicator light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | REF080 |  | REFRIGERATOR, blood, 25 packs per drawer, 2 drawer, with built-in alarm system, external temperature gauge, 1030H 690W 760D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SCN001 |  | SCANNER: Bar-code | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W1584
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | W1584 |  |  |  |  | Store: clinical equipment
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Medical equipment is stored. 2) Large items of equipment are stored. 3) Mobile equipment may be parked and stored and/or recharged. 4) Equipment is placed on charge.
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 16 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | This store includes a mixture of shelving and racking for small equipment and floor space for large equipment.
| ADB | [7 empty] | Room Environmental Data
W1584
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | W1584 |  |  |  |  | Store: clinical equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200/300 |  | Subject to perception of detail required
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W1584
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | W1584 |  |  |  |  | Store: clinical equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W1584
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | W1584 |  |  |  |  | Store: clinical equipment
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 20 |  |  | 20 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PEG005 |  | PEGS, equipment, 3 (500mm spacing), wall mounted | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SHE253 |  | SHELF, 2100W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | CLI017 |  | CLIP, spring, 32mm dia. 3, mounted on a wooden batten, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | SMF011 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 465D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | STO008 |  | STOOL, kick, retractable castors | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W1585
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | W1585 |  |  |  |  | Store: general
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Miscellaneous equipment is stored. 2) Non-clinical supplies are stored.
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2400
Notes:
| ADB | [7 empty] | Room Environmental Data
W1585
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | W1585 |  |  |  |  | Store: general
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200/300 |  | Subject to perception of detail required
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W1585
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | W1585 |  |  |  |  | Store: general
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W1585
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | W1585 |  |  |  |  | Store: general
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 20 |  |  | 20 |  |  |  |  | SHE211 |  | SHELF, 900W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SMF011 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 465D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W1594-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | W1594-01 |  |  |  |  | Store: linen
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Linen and/or towels are stored. 2) Bedding, blankets and pillows are stored. 3) Holding exchange trolley.
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 3 |  |  |  |  | Height (mm): |  |  |  | 2400
Notes:
| ADB | [7 empty] | Room Environmental Data
W1594-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | W1594-01 |  |  |  |  | Store: linen
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W1594-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | W1594-01 |  |  |  |  | Store: linen
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W1594-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | W1594-01 |  |  |  |  | Store: linen
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRO233 |  | TROLLEY, clean linen exchange, 3 adjustable shelves, large, 1600H 1600W 680D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | X1029
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1029 |  |  |  |  | Laboratory: catheter; single plane
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient is transferred to the imaging table. 2) General or local anaesthetic or sedation may be administered. 3) Cardiac investigation - patient undergoes Angiography examination. 4) Contrast media, I.V. injections and other sterile procedures may be prepared. 5) Contrast media may be administered. 6) Physiological monitoring equipment may be used. 7) Recording patient data/notes. 8) Disposal of used gowns. 9) Disposal of waste. 10) Patient may be ambulant, in a wheelchair or on a trolley or bed 11) Emergency resuscitation may take place. 12) Clinical hand washing. 13) Scrub-up trough may be used. 14) Sterile equipment, consumable supplies and packs are stored. 15) Catheters and catheter guide wires used in specialised interventional procedures are stored. 16) Staff notices, information and/or messages may be displayed.
| Personnel: | [6 empty] | 1 x Patient 6 - 8 x Staff
| Planning Relationships: | [5 empty] | Close to cardiac day case unit. Close to CCU & intensive & intermediate care unit. Adjacent to prep/recovery area. Access to scrub-up sink or area
| Space Data: | [6 empty] | Area (m²): |  |  |  | 50 |  |  |  |  | Height (mm): |  |  |  | 3000
| Notes: | [7 empty] | Radiation protection as required. Lighting control panel giving variable levels of illumination. Supplementary imaging by ultrasound may be used. A warming cabinet (wall- or bench-mounted) - project team option. Consideration should be given in appropriate centres to the possible use of this room as a hybrid theatre/imaging room in case of emergency. The Operating Light is shown as gantry mounted - this would be a project option best suited to the manufacturer's euipment and eventual layout. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
X1029
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1029 |  |  |  |  | Laboratory: catheter; single plane
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 22
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Anaesthetic gases in use. Provide clean air flow path
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 1000
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 140000
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | X1029
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1029 |  |  |  |  | Laboratory: catheter; single plane
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 3 sets of doors - radiation protection: 2 x personnel, wheelchair & equipment access (1000mm); 1 x personnel, trolley, wheelchair & equipment access (1700mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Essential Radiation proof glazing to control room Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | X1029
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1029 |  |  |  |  | Laboratory: catheter; single plane
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG033 |  | LUMINAIRE, operating theatre, shadowless, lux 140000 gantry mounted. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | LIG071 |  | ILLUMINATED SIGN 'RADIATION ON', wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG074 |  | ILLUMINATED SIGN "DO NOT ENTER" | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG138 |  | LUMINAIRE, indicating controlled drugs cupboard repeat | [16 empty] | 1
| 13 |  |  | 13 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT454 |  | OUTLET, 7 kPa compressed air, surgical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT461 |  | OUTLET, nitrous oxide, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT480 |  | OUTLET, gas scavenging (AGS), medical | [16 empty] | 1
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | X1029
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1029 |  |  |  |  | Laboratory: catheter; single plane
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | PAN054 |  | PANEL, control invasive imaging procedures, 900H 1200W comprising: 1x Operating lamp ON/OFF switch; 1x Emergency battery lighting"ON"; indicating; 3x General lighting ON/OFF including dimmer switch lamp 1x Standby generator electric mains "ON" indicating lamp; 1x Air temperature indicating gauge 1x Air temperature control 1x Humidity indicating gauge 1x Humidity control and indicating lamp; 1x Ventilation plant "ON"; (NORMAL) indicating lamp 1x Indicating lamp "FILTER REPLACE" 1x Indicating lamp "LOW AIR FLOW" 1x Indicating lamp "MEDICAL GAS FAILURE" 1x Air sampling grille and duct with temperature and humidity sensors 1x Operating list display panel 1x Clock time elapsed 1x Clock synchronous (time of day) 1x Telephone outlet (splash proof) 1x Room "IN USE"; light, ON/OFF switch 1x Room "IN USE"; light, ON/OFF switch 1x Illuminator, x-ray film fixed 1x Illuminator, x-ray film, ON/OFF switch | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PEN044 |  | PENDANT SURGICAL, medical and power supply unit, solo, lateral and vertical movement, ceiling mounted | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SMC053 |  | CABINET, tall, modular storage, for 600 facing inserts, with door, on plinth, 2100H | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC063 |  | CABINET, base, modular storage, for 600 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC073 |  | CABINET, upper, modular storage, for 600 facing inserts, with door, 750H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC121 |  | CATHETER CUPBOARD, 600mm facing, with formed plastic liners, incl. shelf with 5 telescopic rails , 1 door, on plinth, o/a height 2100 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW003 |  | WORKTOP, clinical, for 3 x 600 facing modular storage cabinet, 1965W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | X1029
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1029 |  |  |  |  | Laboratory: catheter; single plane
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | TRO602 |  | TROUGH scrub-up, hospital pattern, stainless steel, double, 75mm upstand, 950H 1600W 450D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CRD121 |  | IMAGE C SUSPENSION Track for ceiling mounted angiography machine, in parallel L4300 | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CRD131 |  | TABLE/COUCH PATIENT, cath. lab, cantilever, radiolucent, floating top, telescoping base, fully adjustable, floor mounted, (Part of CRD121 or CRD122) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS006 |  | DISPENSER, disposable nailbrush, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 3 |  |  | 3 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS432 |  | DISPENSER, disposable hat, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS437 |  | DISPENSER, disposable mask, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG221 |  | MONITOR viewing, flat panel display for image intensifier, ceiling mounted - Bank of 3 | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG223 |  | IMAGE CS ARM swivel, ceiling suspensions for monitors | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG224 |  | IMAGE CS RAIL, ceiling suspensions for monitors, L3500 | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG226 |  | IMAGE GANTRY TRACK in parallel, L3900 | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG231 |  | SHIELD lead acrylic, overhead suspended on bracket, 760W 610D lead equivalent 0.5mm Pb, ceiling mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG241 |  | TRACK, radiation protection screen L2500 | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | RAC196 |  | RACK, x-ray lead apron, 5 hangers hinged, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | ANA004 |  | ANAESTHETIC MACHINE/WORKSTATION with ventilator, with accessories, mobile, 1580H 565W 695D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MON053 |  | MONITOR, multi parameter with gas monitoring, 102H 368W 368D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STA142 |  | STAND, infusion, twin hook, breaks, mobile | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | X1029
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1029 |  |  |  |  | Laboratory: catheter; single plane
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | STO006 |  | STOOL, surgeon/anaesthetist, height adjustable, includes anti-static seat pads | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SYR001 |  | SYRINGE INJECTOR, automatic, hi pressure injection, contrast media | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | TRO133 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 750W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | X1030
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1030 |  |  |  |  | Laboratory: catheter; biplane
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient is transferred to the imaging table. 2) General or local anaesthetic or sedation may be administered. 3) Cardiac investigation - patient undergoes Angiography examination. 4) Contrast media, I.V. injections and other sterile procedures may be prepared. 5) Contrast media may be administered. 6) Physiological monitoring equipment may be used. 7) Recording patient data/notes. 8) Disposal of used gowns. 9) Disposal of waste. 10) Patient may be ambulant, in a wheelchair or on a trolley or bed 11) Emergency resuscitation may take place. 12) Clinical hand washing. 13) Scrub-up trough may be used. 14) Sterile equipment, consumable supplies and packs are stored. 15) Catheters and catheter guide wires used in specialised interventional procedures are stored. 16) Staff notices, information and/or messages may be displayed.
| Personnel: | [6 empty] | 1 x Patient 6 - 8 x Staff
| Planning Relationships: | [5 empty] | Close to cardiac day case unit. Close to CCU & intensive & intermediate care unit. Adjacent to prep/recovery area. Access to scrub-up sink or area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 50 |  |  |  |  | Height (mm): |  |  |  | 3000
| Notes: | [7 empty] | Radiation protection as required. Lighting control panel giving variable levels of illumination. Supplementary imaging by ultrasound may be used. A warming cabinet (wall- or bench-mounted) - project team option. Consideration should be given in appropriate centres to the possible use of this room as a hybrid theatre/imaging room in case of emergency. The Operating Light is shown as gantry mounted - this would be a project option best suited to the manufacturer's euipment and eventual layout. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
X1030
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1030 |  |  |  |  | Laboratory: catheter; biplane
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 22
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Anaesthetic gases in use. Provide clean air flow path
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 1000
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 140000
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | X1030
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1030 |  |  |  |  | Laboratory: catheter; biplane
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 3 sets of doors - radiation protection: 2 x personnel, wheelchair & equipment access (1000mm); 1 x personnel, trolley, wheelchair & equipment access (1700mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Essential Radiation proof glazing to control room Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | X1030
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1030 |  |  |  |  | Laboratory: catheter; biplane
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG033 |  | LUMINAIRE, operating theatre, shadowless, lux 140000 gantry mounted. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | LIG071 |  | ILLUMINATED SIGN 'RADIATION ON', wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG074 |  | ILLUMINATED SIGN "DO NOT ENTER" | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG138 |  | LUMINAIRE, indicating controlled drugs cupboard repeat | [16 empty] | 1
| 13 |  |  | 13 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT454 |  | OUTLET, 7 kPa compressed air, surgical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT461 |  | OUTLET, nitrous oxide, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT480 |  | OUTLET, gas scavenging (AGS), medical | [16 empty] | 1
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | X1030
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1030 |  |  |  |  | Laboratory: catheter; biplane
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | PAN054 |  | PANEL, control invasive imaging procedures, 900H 1200W comprising: 1x Operating lamp ON/OFF switch; 1x Emergency battery lighting"ON"; indicating; 3x General lighting ON/OFF including dimmer switch lamp 1x Standby generator electric mains "ON" indicating lamp; 1x Air temperature indicating gauge 1x Air temperature control 1x Humidity indicating gauge 1x Humidity control and indicating lamp; 1x Ventilation plant "ON"; (NORMAL) indicating lamp 1x Indicating lamp "FILTER REPLACE" 1x Indicating lamp "LOW AIR FLOW" 1x Indicating lamp "MEDICAL GAS FAILURE" 1x Air sampling grille and duct with temperature and humidity sensors 1x Operating list display panel 1x Clock time elapsed 1x Clock synchronous (time of day) 1x Telephone outlet (splash proof) 1x Room "IN USE"; light, ON/OFF switch 1x Room "IN USE"; light, ON/OFF switch 1x Illuminator, x-ray film fixed 1x Illuminator, x-ray film, ON/OFF switch | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PEN044 |  | PENDANT SURGICAL, medical and power supply unit, solo, lateral and vertical movement, ceiling mounted | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SMC053 |  | CABINET, tall, modular storage, for 600 facing inserts, with door, on plinth, 2100H | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC063 |  | CABINET, base, modular storage, for 600 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SMC073 |  | CABINET, upper, modular storage, for 600 facing inserts, with door, 750H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC121 |  | CATHETER CUPBOARD, 600mm facing, with formed plastic liners, incl. shelf with 5 telescopic rails , 1 door, on plinth, o/a height 2100 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW003 |  | WORKTOP, clinical, for 3 x 600 facing modular storage cabinet, 1965W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | X1030
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1030 |  |  |  |  | Laboratory: catheter; biplane
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | TRO602 |  | TROUGH scrub-up, hospital pattern, stainless steel, double, 75mm upstand, 950H 1600W 450D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CRD121 |  | IMAGE C SUSPENSION Track for ceiling mounted angiography machine, in parallel L4300 | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CRD122 |  | ANGIOGRAPHY MACHINE, bi-plane, C-arm multi-angular isocentric x-ray system, ceiling mounted (in conjunction with CRD121) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CRD131 |  | TABLE/COUCH PATIENT, cath. lab, cantilever, radiolucent, floating top, telescoping base, fully adjustable, floor mounted, (Part of CRD121 or CRD122) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS006 |  | DISPENSER, disposable nailbrush, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 3 |  |  | 3 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS432 |  | DISPENSER, disposable hat, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS437 |  | DISPENSER, disposable mask, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG222 |  | MONITOR viewing, flat panel display for image intensifier, ceiling mounted - Bank of 6 | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG223 |  | IMAGE CS ARM swivel, ceiling suspensions for monitors | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG224 |  | IMAGE CS RAIL, ceiling suspensions for monitors, L3500 | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG226 |  | IMAGE GANTRY TRACK in parallel, L3900 | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG229 |  | IMAGE C SUSPENSION Track for ceiling mounted angiography machine, in parallel L4300 | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG231 |  | SHIELD lead acrylic, overhead suspended on bracket, 760W 610D lead equivalent 0.5mm Pb, ceiling mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG241 |  | TRACK, radiation protection screen L2500 | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | ANA004 |  | ANAESTHETIC MACHINE/WORKSTATION with ventilator, with accessories, mobile, 1580H 565W 695D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | X1030
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1030 |  |  |  |  | Laboratory: catheter; biplane
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | MON053 |  | MONITOR, multi parameter with gas monitoring, 102H 368W 368D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STA142 |  | STAND, infusion, twin hook, breaks, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STO006 |  | STOOL, surgeon/anaesthetist, height adjustable, includes anti-static seat pads | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SYR001 |  | SYRINGE INJECTOR, automatic, hi pressure injection, contrast media | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | TRO133 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 750W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | X1031
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1031 |  |  |  |  | Control area: serving catheter laboratory
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Using the operating console to control each scan and monitor the VDT image. 2) Communication with colleagues/offices/departments may occur by telephone. 3) Test results are recorded 4) Observation is undertaken by medical and nursing staff. 5) Writing notes. 6) Small items of equipment are held stored 7) Stationery/paper is stored. 8) Reference books, literature and information may be held/stored.
| Personnel: | [6 empty] | 3 - 4 x Staff
| Planning Relationships: | [5 empty] | En-suite to catheter laboratory room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | Good visual & voice contact with the laboratory. Radiation protection as required. Three computer workstations are required; one each for use by a physiologist, and/or visiting specialist (to observe procedures and take notes) and the other (which supports the X-ray controls) for use by a radiographer. A minimum of three computer workstations are required per laboratory. 2 for control and capture of images and monitoring of other data, and one for use by the physiologist or or other clinician viewinig/monitoring the procedure. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
X1031
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1031 |  |  |  |  | Control area: serving catheter laboratory
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 22
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | X1031
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1031 |  |  |  |  | Control area: serving catheter laboratory
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - radiation protection: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Essential Radiation proof glazing to control room Roller blind on cath. lab. room side Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | X1031
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1031 |  |  |  |  | Control area: serving catheter laboratory
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 9 |  |  | 9 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW083 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 2300W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW087 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 2700W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | RAC089 |  | RACK, leaflet/pamphlet, 4 sections, with adjustable dividers, wall mounted, 300H 805W 215D | [16 empty] | 2
| 4 |  |  | 4 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 5 |  |  | 5 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | COM050 |  | COMPUTER MONITOR, 18''; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | X1031-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1031-01 |  |  |  |  | Control area: serving 2 catheter laboratories
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Using the operating console to control each scan and monitor the VDT image. 2) Communication with colleagues/offices/departments may occur by telephone. 3) Test results are recorded 4) Observation is undertaken by medical and nursing staff. 5) Writing notes. 6) Small items of equipment are held stored 7) Stationery/paper is stored. 8) Reference books, literature and information may be held/stored.
| Personnel: | [6 empty] | 6 - 8 x Staff
| Planning Relationships: | [5 empty] | En-suite to catheter laboratory room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 20 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | Good visual & voice contact with the laboratory. Radiation protection as required. Three computer workstations are required; one each for use by a physiologist, and/or visiting specialist (to observe procedures and take notes) and the other (which supports the X-ray controls) for use by a radiographer. A minimum of three computer workstations are required per laboratory. 2 for control and capture of images and monitoring of other data, and one for use by the physiologist or or other clinician viewinig/monitoring the procedure. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
X1031-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1031-01 |  |  |  |  | Control area: serving 2 catheter laboratories
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 22
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | X1031-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1031-01 |  |  |  |  | Control area: serving 2 catheter laboratories
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors - radiation protection: 2 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required - windows not desirable
Internal Glazing:
Essential Radiation proof glazing to control room Roller blind on cath. lab. room side Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | X1031-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1031-01 |  |  |  |  | Control area: serving 2 catheter laboratories
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 14 |  |  | 14 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 15 |  |  | 15 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMW078 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 1800W 700D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMW087 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 2700W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | RAC089 |  | RACK, leaflet/pamphlet, 4 sections, with adjustable dividers, wall mounted, 300H 805W 215D | [16 empty] | 2
| 6 |  |  | 6 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 8 |  |  | 8 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 12 |  |  | 12 |  |  |  |  | COM050 |  | COMPUTER MONITOR, 18''; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | X1035
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1035 |  |  |  |  | Minor cardiac procedures room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patient may arrive on foot or in a wheelchair. 2) Patient is transferred to a couch or treatment trolley/chair 3) Administration of local analgesics. 4) Minor surgical procedures may be performed under local anaesthetic. 5) Implantable devices may be inserted or replaced. 6) Minimally invasive clinical procedures may be undertaken from one or both sides of the couch. 7) Visual display terminal(s) may be used. 8) Administration of general anaesthetic.
| Personnel: | [6 empty] | 1 x patient 3-4 x staff
| Planning Relationships: | [5 empty] | Close to cardiac day case unit. Close to CCU & intensive & intermediate care unit. Adjacent to prep/recovery area. Close to scrub-up sink or area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 28 |  |  |  |  | Height (mm): |  |  |  | 2950
| Notes: | [7 empty] | Radiation protection as required. Lighting control panel giving variable levels of illumination. Supplementary imaging by ultrasound may be used. A warming cabinet (wall- or bench-mounted) - project team option. If a keyboard is used with the monitor it is recommended that a suitable washable cover is provided for infection control purposes. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
X1035
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1035 |  |  |  |  | Minor cardiac procedures room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | +ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
Type Of Control:
Daytime General Service Illuminance (Lux):
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | N
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | X1035
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1035 |  |  |  |  | Minor cardiac procedures room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - radiation protection: 1 x personnel, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | X1035
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1035 |  |  |  |  | Minor cardiac procedures room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG050 |  | LUMINAIRE operating (minor) | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG071 |  | ILLUMINATED SIGN 'RADIATION ON', wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG074 |  | ILLUMINATED SIGN "DO NOT ENTER" | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG138 |  | LUMINAIRE, indicating controlled drugs cupboard repeat | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 16 |  |  | 16 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT050 |  | OUTLET, controlled drugs cupboard | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT056 |  | CONNECTION UNIT, unswitched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT454 |  | OUTLET, 7 kPa compressed air, surgical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT461 |  | OUTLET, nitrous oxide, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT480 |  | OUTLET, gas scavenging (AGS), medical | [16 empty] | 1
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | X1035
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1035 |  |  |  |  | Minor cardiac procedures room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | PAN054 |  | PANEL, control invasive imaging procedures, 900H 1200W comprising: 1x Operating lamp ON/OFF switch; 1x Emergency battery lighting"ON"; indicating; 3x General lighting ON/OFF including dimmer switch lamp 1x Standby generator electric mains "ON" indicating lamp; 1x Air temperature indicating gauge 1x Air temperature control 1x Humidity indicating gauge 1x Humidity control and indicating lamp; 1x Ventilation plant "ON"; (NORMAL) indicating lamp 1x Indicating lamp "FILTER REPLACE" 1x Indicating lamp "LOW AIR FLOW" 1x Indicating lamp "MEDICAL GAS FAILURE" 1x Air sampling grille and duct with temperature and humidity sensors 1x Operating list display panel 1x Clock time elapsed 1x Clock synchronous (time of day) 1x Telephone outlet (splash proof) 1x Room "IN USE"; light, ON/OFF switch 1x Room "IN USE"; light, ON/OFF switch 1x Illuminator, x-ray film fixed 1x Illuminator, x-ray film, ON/OFF switch | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PEN044 |  | PENDANT SURGICAL, medical and power supply unit, solo, lateral and vertical movement, ceiling mounted | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMW072 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 1200W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SUC002 |  | SUCTION UNIT, pipeline, high pressure, theatre | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BRA003 |  | BRACKET, holder, suction unit. | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB064 |  | CABINET, metal, controlled drugs, 1 door, lockable, with warning light, wall mounted, 550H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG021 |  | IMAGE INTENSIFIER UNIT, C-arm, mobile | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG023 |  | IMAGE INTENSIFIER, monitor, (Part of IMG021) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | IMG024 |  | IMAGE INTENSIFIER, monitor trolley, (Part of IMG021) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | COM047 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, touch screen, desk top | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | X1035
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | X1035 |  |  |  |  | Minor cardiac procedures room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | HOL014 |  | HOLDER, sack, with lid foot operated, large, capacity 120 litre, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | INF002 |  | INFUSION volumetric pump, 188H 110W 60D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MON013 |  | MONITOR, vital signs, multi-parameter, with accessories, 280H 360W 215D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC197 |  | RACK, x-ray lead apron, 6 swivel arms, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STA142 |  | STAND, infusion, twin hook, breaks, mobile | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | STO006 |  | STOOL, surgeon/anaesthetist, height adjustable, includes anti-static seat pads | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB071 |  | TABLE operating patient, powered with 250mm transverse top, complete with specialty accessories, 715H 600W 2102D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO131 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 450W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO133 |  | TROLLEY, dressing/instrument, stainless steel, buffered, 870H 750W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO201 |  | TROLLEY, instruments, stainless steel, buffered, 870H 920W 620D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO204 |  | TROLLEY instrument tray MAYO, 650W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0331
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0331 |  |  |  |  | Dirty utility room: bedpan processing
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Disposal of liquid waste. 2) Disposal of bedpans, urine bottles and vomit bowls with contents. 3) Cleansing bedpan holders. 4) Holding/storing working supplies of disposable bedpans, urine bottles and vomit bowls. 5) Holding SHARPS in a container. 6) Items requiring disposal or reprocessing may be held/stored. 7) Holding dirty linen. 8) Sani-chairs and commodes may be parked and/or stored. 9) Clinical wash-hand basin may be used. 10) Urine specimens may be tested. 11) Clinical waste may be disposed 12) Disposal of waste and contaminated materials. 13) Disposal of used protective clothing. 14) Disposal of non-clinical waste.
| Personnel: | [6 empty] | 2 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Close to clinical area, particularly treatment rooms.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The following items may be provided: - placenta weighing scales.
| ADB | [7 empty] | Room Environmental Data
Y0331
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0331 |  |  |  |  | Dirty utility room: bedpan processing
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0331
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0331 |  |  |  |  | Dirty utility room: bedpan processing
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0331
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0331 |  |  |  |  | Dirty utility room: bedpan processing
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU001 |  | DISPOSAL UNIT (macerator), disposable bedpan, bedpan liners/urine bottles, 525W 650D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU006 |  | DISPOSAL UNIT, plain top, right hand drainer, with sink and hopper with flushing rim, 110mm outlet, no tap holes no overflow, back inlet, stainless steel, 1600W 600D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT079 |  | OUTLET isolator, equipment manufacturer's specification | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT301 |  | OUTLET, cold water for equipment | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC023 |  | CABINET, upper, modular storage, for 400 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW052 |  | WORKTOP, clinical, for 2 x 400 facing modular storage cabinets, 910W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS004 |  | DISPENSER, disposable bedpans, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS005 |  | DISPENSER, disposable urine bottles, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS007 |  | DISPENSER, paper towel roll, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS442 |  | DISPENSER, vomit bowls, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | RAC001 |  | RACK, drainage, bedpan holder (5), with drip tray, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CHA338 |  | SANI-CHAIR/COMMODE, tubular, metal, wipeable, mobile. | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0331
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0331 |  |  |  |  | Dirty utility room: bedpan processing
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0436
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0436 |  |  |  |  | Dirty utility room: theatre
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Disposal of liquid waste. 2) Holding SHARPS in a container. 3) Items requiring disposal or reprocessing may be held/stored. 4) SSD returns trolley is parked/stored. 5) Clinical wash-hand basin may be used. 6) Clinical waste may be disposed 7) Disposal of used protective clothing. 8) Disposal of non-clinical waste. 9) Emptying buckets, etc. 10) Disposal of used packaging materials.
| Personnel: | [6 empty] | 2 x Staff.
| Planning Relationships: | [5 empty] | Direct access from theatre and corridor.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
Y0436
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0436 |  |  |  |  | Dirty utility room: theatre
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | >20
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | n/a
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0436
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0436 |  |  |  |  | Dirty utility room: theatre
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0436
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0436 |  |  |  |  | Dirty utility room: theatre
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU006 |  | DISPOSAL UNIT, plain top, right hand drainer, with sink and hopper with flushing rim, 110mm outlet, no tap holes no overflow, back inlet, stainless steel, 1600W 600D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE211 |  | SHELF, 900W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC023 |  | CABINET, upper, modular storage, for 400 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW052 |  | WORKTOP, clinical, for 2 x 400 facing modular storage cabinets, 910W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLI017 |  | CLIP, spring, 32mm dia. 3, mounted on a wooden batten, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS007 |  | DISPENSER, paper towel roll, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL014 |  | HOLDER, sack, with lid foot operated, large, capacity 120 litre, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL020 |  | HOLDER, sharps box, up to 7 litre capacity, rail/trolley hang or wall mounted, 170H 125W 100D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO024 |  | TROLLEY cleaners, bucket, disposable mop head | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO207 |  | TROLLEY SSD return, 2 door, nominal 970H 1140W 725D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0511
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0511 |  |  |  |  | Utility: footwear washing
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Cleaning footwear in machine.
| Personnel: | [6 empty] | 1 person intermittently
| Planning Relationships: | [5 empty] | Close to staff changing facilities within theatres or catheter laboratories
| Space Data: | [6 empty] | Area (m²): |  |  |  | 4 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
Y0511
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0511 |  |  |  |  | Utility: footwear washing
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0511
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0511 |  |  |  |  | Utility: footwear washing
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0511
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0511 |  |  |  |  | Utility: footwear washing
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | COC001 |  | STOP COCK/PLUG VALVE, ball-o-fix | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT341 |  | OUTLET, drainage, anti-syphon | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW066 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 600W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAS037 |  | WASHING MACHINE, footwear, 850H 900W 660D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0642
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0642 |  |  |  |  | Disposal hold: 1700 litres
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Holding domestic, clinical and recyclable waste for disposal or reprocessing
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Adjacent to main circulation route.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2700
Ceiling height must allow bin lids to open fully.
| Notes: | [7 empty] | Separate bins/areas must be provided for: - clinical waste; - domestic waste; - recyclable items; - linen; - equipment requiring reprocessing.
| ADB | [7 empty] | Room Environmental Data
Y0642
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0642 |  |  |  |  | Disposal hold: 1700 litres
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0642
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0642 |  |  |  |  | Disposal hold: 1700 litres
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley, & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0642
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0642 |  |  |  |  | Disposal hold: 1700 litres
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BIN034 |  | BIN wheelie, 240 litre, 1060H 600W 730D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | BIN038 |  | BIN wheelie, 1100 litre, 1470H1370W 1115D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0646
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0646 |  |  |  |  | Disposal hold: 3000 litres
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Holding domestic, clinical and recyclable waste for disposal or reprocessing
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Adjacent to main circulation route.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
Ceiling height must allow bin lids to open fully.
| Notes: | [7 empty] | Separate bins/areas must be provided for: - clinical waste; - domestic waste; - recyclable items; - linen; - equipment requiring reprocessing.
| ADB | [7 empty] | Room Environmental Data
Y0646
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0646 |  |  |  |  | Disposal hold: 3000 litres
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0646
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0646 |  |  |  |  | Disposal hold: 3000 litres
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0646
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y0646 |  |  |  |  | Disposal hold: 3000 litres
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BIN037 |  | BIN wheelie, 770 litre, 1360H1360W 800D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Disposal of liquid waste. 2) Filling and emptying cleaning equipment and containers. 3) Holding/storing cleaning equipment. 4) Cleaning equipment may be parked and/or stored. 5) Hand-rinse basin may be used. 6) Sink may be used. 7) Janitorial unit may be used.
| Personnel: | [6 empty] | 2 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Close to areas served.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
If large equipment is stored elsewhere, the size of this room can be reduced.
| Notes: | [7 empty] | This room represents a typical traditional cleaners' room with space for storing a vacuum cleaner, scrubbing/polishing machine (for hard floors) and mop and bucket (stored on the cleaners' trolley). It includes a combined bucket sink and hand-rinse basin (janitorial unit) and separate sink. The following items are shown on the room layout but are optional: - small cube lockers.
| ADB | [7 empty] | Room Environmental Data
Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 22
| Unified Glare Rating Limit (UGRL): | [13 empty] | 80
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Heat
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | CARD |  |  |  |  | Facilities for Cardiac Services Design Guidance Manuals: Cardiac Operating Theatres v:0.2: England and Minor Cardiac Procedures Suite:v:0.2 : England - list of spaces
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | HOO020 |  | HOOK, single, large, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE231 |  | SHELF, 1500W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SIN013 |  | SINK and BASIN combination Janitorial unit, hinged bucket grating to sink and monobloc mixer tap with swivel nozzle, stainless steel, 900H 500W 600D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SNU012 |  | SINK UNIT, single bowl with right hand drainer, no tap holes, 1200W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLI017 |  | CLIP, spring, 32mm dia. 3, mounted on a wooden batten, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | LOC012 |  | LOCKER, wall mounted, 340H 300W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLE008 |  | SCRUBBING/POLISHING MACHINE, single brush, 110v machine | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CLE018 |  | CLEANER VACUUM, dry suction, tub, with accessories, filtered air exhaust | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | CON061 |  | CONE, warning, 'wet floor' | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL014 |  | HOLDER, sack, with lid foot operated, large, capacity 120 litre, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAD002 |  | LADDER, 3 tread, platform type 750mm height, folding | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO068 |  | TROLLEY, cleaners, mop bucket, 3 shelves tray and waste sack holder, 980H 1170W 550D | [16 empty] | 3
Activity DataBase
2016-12-28