## Sheet1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | D0205
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | D0205 |  |  |  |  | Rest room with beverage, snack preparation bay: 5 staff
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Rest and relaxation or sleeping. 2) Patient, relative or staff may be reading. 3) Preparing beverages and snacks. 4) Consuming beverages, meals and snacks. 5) Holding/ storing food in refrigerator. 6) Holding crockery and cutlery. 7) Washing up of crockery and cutlery. 8) Staff notices, information and/or messages may be displayed. 9) Informal staff discussions. 10) Hand washing.
| Personnel: | [6 empty] | 5 x Staff
| Planning Relationships: | [5 empty] | Part of staff accommodation.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 11 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
D0205
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | D0205 |  |  |  |  | Rest room with beverage, snack preparation bay: 5 staff
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 – 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V/EM
| Daytime General Service Illuminance (Lux): | [13 empty] | 50 |  | Floor
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 200 |  | On tables
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 300 |  | At servery counter
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | D0205
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | D0205 |  |  |  |  | Rest room with beverage, snack preparation bay: 5 staff
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | D0205
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | D0205 |  |  |  |  | Rest room with beverage, snack preparation bay: 5 staff
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAT002 |  | MINI KITCHEN (combined unit) with refrigerator and microwave, sink top, wall cabinet, cupboard and drawers, laminate backboard, 1970H 1200W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC073 |  | CABINET, upper, modular storage, for 600 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAT003 |  | WATER BOILER, 2.5 litre, electric, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | RAC091 |  | RACK, magazine, 3 shelves, floor standing, fixed to the wall, 1400H 900W 300D | [16 empty] | 2
| 3 |  |  | 3 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA318 |  | CHAIR, upright, with arms, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB056 |  | TABLE, occasional, round, 415H 610mm dia. | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0171
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | G0171 |  |  |  |  | Parking bay: large equipment
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Parking equipment. 2) Equipment is placed on charge.
| Personnel: | [6 empty] | Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 4 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
G0171
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | G0171 |  |  |  |  | Parking bay: large equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | See HVAC notes 2
| Ventilation Type: | [13 empty] | N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
| General Notes: | [5 empty] | Part of corridor space
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0171
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | G0171 |  |  |  |  | Parking bay: large equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0171
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | G0171 |  |  |  |  | Parking bay: large equipment
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0505
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | G0505 |  |  |  |  | Post-mortem room transit area with staff changing Gowning, boot wash floor tray
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Changing into/out of protective clothing. 2) Changing footwear. 3) Storing protective clothing. 4) Storing disposable plastic aprons and boots/footwear. 5) Dispensing disposable aprons. 6) Disposal of used protective clothing. 7) Washing, disinfecting footwear in a tray. 8) Clinical hand washing/scrubbing. 9) Holding used protective clothing or overalls. 10) Holding used protective footwear.
| Personnel: | [6 empty] | Intermittent use
| Planning Relationships: | [5 empty] | Staff pass through a boot wash floor tray. Dual access between P.M. room & staff change, WC/shower facilities. Access to clean and dirty activity areas.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 10 |  |  |  |  | Height (mm): |  |  |  | 2400
Notes:
| ADB | [7 empty] | Room Environmental Data
G0505
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | G0505 |  |  |  |  | Post-mortem room transit area with staff changing Gowning, boot wash floor tray
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 – 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | +Ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
Type Of Control:
Daytime General Service Illuminance (Lux):
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0505
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | G0505 |  |  |  |  | Post-mortem room transit area with staff changing Gowning, boot wash floor tray
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 3 sets of doors: 3 x personnel access (900mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0505
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | G0505 |  |  |  |  | Post-mortem room transit area with staff changing Gowning, boot wash floor tray
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | TRA041 |  | TRAY wash/disinfect footwear, floor recessed | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL007 |  | HOLDER, sack, large, capacity 120 litre, freestanding | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC023 |  | RACK, boot, 6 places, 900H 900W 400D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0710
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | G0710 |  |  |  |  | Telephone booth
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Payphone may be used.
| Personnel: | [6 empty] | 1 x person.
| Planning Relationships: | [5 empty] | Within easy access.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 1.5 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | All public telephones should include a shelf to enable a person with a hearing impairment to use a portable text phone. The following items are shown on the room layout but are optional: - acoustic hood. - Where provided, it should be designed and mounted in such a way that it is not a hazard to disabled people i.e. by ensuring that it is located outside any circulation route or by provision of a hazard warning.
| ADB | [7 empty] | Room Environmental Data
G0710
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | G0710 |  |  |  |  | Telephone booth
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | n/a
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 100
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 300 |  | On telephone
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 43
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 43 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0710
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | G0710 |  |  |  |  | Telephone booth
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0710
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | G0710 |  |  |  |  | Telephone booth
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT220 |  | SOCKET, outlet telephone, part of TEL004 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TEL004 |  | TELEPHONE handset coin/card operated, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | TEL019 |  | TELEPHONE HOOD, acoustic, wall mounted | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0712
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | G0712 |  |  |  |  | Telephone booth: wheelchair accessible
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Payphone may be used.
| Personnel: | [6 empty] | 1 x person.
| Planning Relationships: | [5 empty] | Within easy access.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | Telephones for wheelchair users should be located to enable access from the front and side. This is assumed in the room layout. Where it is only possible to approach the telephone from the front, a knee hole at least 500 mm deep and 700 mm high should be provided This space includes a fold-down seat (450-520 mm high), alternatively, it can accommodate a perch seat (650-800 mm high) for ambulant users only.
| ADB | [7 empty] | Room Environmental Data
G0712
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | G0712 |  |  |  |  | Telephone booth: wheelchair accessible
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | n/a
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 100
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 300 |  | On telephone
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 44
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 44 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0712
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | G0712 |  |  |  |  | Telephone booth: wheelchair accessible
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0712
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | G0712 |  |  |  |  | Telephone booth: wheelchair accessible
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT220 |  | SOCKET, outlet telephone, part of TEL004 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | RAI046 |  | RAIL, grab, vertical, wall mounted, 450mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SEA024 |  | SEAT, tip-up, wall mounted, 400 W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TEL004 |  | TELEPHONE handset coin/card operated, wall mounted | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | J1255
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | J1255 |  |  |  |  | Waiting area: 5 places (including 1 wheelchair place)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patients, relatives and escorts wait to be seen. 2) Displaying information.
| Personnel: | [6 empty] | 5 x persons, including 1 x wheelchair user
| Planning Relationships: | [5 empty] | Close to clinical or work area. Close to WC facilities.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 9 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design. .
| Notes: | [7 empty] | Type of seating to be suitable for patient profile. Method for calling patients into clinical rooms to be decided locally. The following items may be provided: - an enclosed noticeboard; - background music and other entertainment facilities; - television and internet access.
| ADB | [7 empty] | Room Environmental Data
J1255
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | J1255 |  |  |  |  | Waiting area: 5 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | -
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 65
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 65 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | J1255
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | J1255 |  |  |  |  | Waiting area: 5 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control or Not applicable Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | J1255
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | J1255 |  |  |  |  | Waiting area: 5 places (including 1 wheelchair place)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAC089 |  | RACK, leaflet/pamphlet, 4 sections, with adjustable dividers, wall mounted, 300H 805W 215D | [16 empty] | 2
| 4 |  |  | 4 |  |  |  |  | CHA367 |  | UNIT CHAIR, 1 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | J1255-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | J1255-01 |  |  |  |  | Waiting area: 10 places (including 1 wheelchair place)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Patients, relatives and escorts wait to be seen. 2) Displaying information.
| Personnel: | [6 empty] | 10 x persons, including 1 x wheelchair user.
| Planning Relationships: | [5 empty] | Close to clinical or work area. Close to WC facilities.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 15 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | Type of seating to be suitable for patient profile. Method for calling patients into clinical rooms to be decided locally. The following items may be provided: - an enclosed noticeboard; - background music and other entertainment facilities; - television and internet access.
| ADB | [7 empty] | Room Environmental Data
J1255-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | J1255-01 |  |  |  |  | Waiting area: 10 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | -
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 66
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 66 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | J1255-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | J1255-01 |  |  |  |  | Waiting area: 10 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control or Not applicable Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | J1255-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | J1255-01 |  |  |  |  | Waiting area: 10 places (including 1 wheelchair place)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAC089 |  | RACK, leaflet/pamphlet, 4 sections, with adjustable dividers, wall mounted, 300H 805W 215D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | RAC091 |  | RACK, magazine, 3 shelves, floor standing, fixed to the wall, 1400H 900W 300D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CHA367 |  | UNIT CHAIR, 1 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA368 |  | UNIT CHAIR, 2 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA369 |  | UNIT CHAIR, 3 seater, with arms, upholstered, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1602
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1602 |  |  |  |  | Medical observation area, 6 - 8 person Mortuary
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Observing and recording of post-mortem findings.
| Personnel: | [6 empty] | Intermittent use
| Planning Relationships: | [5 empty] | No direct access to Post-Mortem room. Overlooking cutting-up benches & P.M. tables.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | Video/two-way communication system to enabling two-way speech to PM Room if full glazed screen between. Partially open glazed divider to the PM room with an angled observation screen to the dissecting table - project team option. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
L1602
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1602 |  |  |  |  | Medical observation area, 6 - 8 person Mortuary
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1602
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1602 |  |  |  |  | Medical observation area, 6 - 8 person Mortuary
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm)
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Essential Glazed screen to Post Mortem room Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1602
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1602 |  |  |  |  | Medical observation area, 6 - 8 person Mortuary
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WKT136 |  | WORKTOP, cantilevered from wall, 3000W 550D | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | STO007 |  | STOOL, metal frame, upholstered, 710 height | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1607
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1607 |  |  |  |  | Dirty utility and instrument store Mortuary
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Storage of instruments. 2) Containers are stored. 3) Soiled instruments may be cleansed, disinfected and sterilised 4) Preparation of chemical solutions. 5) Storing chemicals. 6) Clinical hand washing.
Personnel:
| Planning Relationships: | [5 empty] | Direct access to Post-Mortem room. Direct access to disposal hold.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | In Mortuary - All socket outlets should be fed via a safe supply unit & be splash-proof - Ref. to text guide.
| ADB | [7 empty] | Room Environmental Data
L1607
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1607 |  |  |  |  | Dirty utility and instrument store Mortuary
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN20
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1607
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1607 |  |  |  |  | Dirty utility and instrument store Mortuary
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel, trolley & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1607
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1607 |  |  |  |  | Dirty utility and instrument store Mortuary
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU013 |  | DISPOSAL UNIT, hopper with flushing rim, 110mm outlet, no tap holes no overflow, back inlet, stainless steel, 900H 600W 600D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | GRI131 |  | GRILLE extract, flush mounted vent, plenum box, 150H 600W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT030 |  | SOCKET outlet switched 13amp single, splashproof | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT032 |  | SOCKET outlet switched 13amp double, splashproof | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT053 |  | CONNECTION UNIT switched 13amp, splashproof. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT351 |  | OUTLET, floor drainage and grating, 400W 400D, general pattern. HTM64FOG | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SIN039 |  | SINK, double bowl and drainers flat, stainless steel, 250H 2400W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW075 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 1500W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP001 |  | TAP extension piece(bib/pillar), length to suit | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP824 |  | TAP bib 2x12mm, mixer, double, hose outlet and pistol grip valve control | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP894 |  | TAP bib, hospital pattern, integral thermostatic mixer, automatic action with sensor operation. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAS060 |  | WASHER/DISINFECTOR, high temperature, 845H 745W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DRY004 |  | DRYER, hand/face, non-touch action, electric, 210H 260W 240D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | RAI003 |  | RAIL, apron hanging, fitted with 10 hooks, 1200W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP205 |  | CUPBOARD, mild steel EPC finish, glass front, lockable, 1520H 910W 400D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STO007 |  | STOOL, metal frame, upholstered, 710 height | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRA051 |  | TRAY, drip, 100H 1300W 250D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1609
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1609 |  |  |  |  | Bier room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Placing of bodies for viewing or identification. 2) Placing flowers or items of religious significance for viewing. 3) Relatives need to enter Bier room.
Personnel:
| Planning Relationships: | [5 empty] | Interconnecting doors to viewing room & body handling area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 10 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | Dimming of lights to be controlled from Bier and Viewing room. Lighting to be aesthetic as well as functional.
| ADB | [7 empty] | Room Environmental Data
L1609
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1609 |  |  |  |  | Bier room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN20
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 30-150
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1609
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1609 |  |  |  |  | Bier room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 1 x personnel access (900mm); 1 x personnel, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Essential Viewing sliding window, clear glass, privacy control. Height suitable for wheelchair users Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1609
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1609 |  |  |  |  | Bier room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE220 |  | SHELF, 1200W 200D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC031 |  | SWITCH dimmer, fixed position, wall mounted | [16 empty] | 1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1610
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1610 |  |  |  |  | Body viewing room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Viewing bodies for identification. 2) Viewing of body by relatives via glazed panel/window. 3) Relatives need to enter Bier room.
| Personnel: | [6 empty] | 2 - 4 Persons
| Planning Relationships: | [5 empty] | With connecting doors to waiting room & bier room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | Lighting to be aesthetic as well as functional.
| ADB | [7 empty] | Room Environmental Data
L1610
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1610 |  |  |  |  | Body viewing room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN20
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 30-150 |  | Domestic type lighting
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | High
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1610
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1610 |  |  |  |  | Body viewing room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Essential Viewing sliding window, clear glass, privacy control. Height suitable for wheelchair users Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1610
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1610 |  |  |  |  | Body viewing room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE240 |  | SHELF, 1800W 200D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC031 |  | SWITCH dimmer, fixed position, wall mounted | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CHA367 |  | UNIT CHAIR, 1 seater, with arms, upholstered, wipeable | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1613
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1613 |  |  |  |  | Body store and handling area: 2 bays single ended, 10 bodies
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Receiving bodies on trolley. 2) Identify and label body, enter details in record book or computer. 3) Placing of shrouds on body. 4) Transfer of bodies to the refrigerated body store. 5) Holding of bodies in the refrigerated body store. 6) Removal of body from store to Bier room. 7) Removal of body from store for handing over to undertakers. 8) Parking hoist. 9) Equipment trolley(s) may be parked and/or stored. 10) Placing valuables in sealed container. 11) Clinical hand washing.
Personnel:
| Planning Relationships: | [5 empty] | Adjacent to Bier room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 18 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Bell push/two-way communication system linked from mortuary entrance - project team option. If bodies are to be prepared and/or undressed in the body handling area, there should be at least one screened bay to provide some privacy. Refrigeration unit located in adjacent plant room. In Isolation section of mortuary design to take account of 'frost heave' precautions; 'anti-freeze' water mats at door seals; evaporator coil defrost requirements. Thermostatic control will be required for each compartment bay. Facilities should be provided to enable compartment bays not in use to be switched off. All socket outlets should be fed via a safe supply unit & be splash-proof - Ref. to text guide. For radioactive body handling & store requirements; ref. to Text Guide Appendix II. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
L1613
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1613 |  |  |  |  | Body store and handling area: 2 bays single ended, 10 bodies
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN20
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200 |  | Suitable for use in low ambient temperatures
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1613
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1613 |  |  |  |  | Body store and handling area: 2 bays single ended, 10 bodies
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 1 x personnel, bed, trolley, wheelchair & equipment access (1500mm) 1 x personnel, bed, trolley, wheelchair & equipment access (1900mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1613
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1613 |  |  |  |  | Body store and handling area: 2 bays single ended, 10 bodies
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD033 |  | BODY STORE, 4 deg.C, 3 - 5 tier adjustable, single ended, right hand bay, lockable, nominal 2600H 900W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD036 |  | BODY STORE, 4 deg.C, extra wide, 3 - 5 tier adjustable, single ended, left hand bay, lockable, nominal 2600H 1100W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL028 |  | BELL, call, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT032 |  | SOCKET outlet switched 13amp double, splashproof | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT351 |  | OUTLET, floor drainage and grating, 400W 400D, general pattern. HTM64FOG | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA363 |  | CHAIR, height adjustable, with arms, high back, swivel, 5 star base, wipeable, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DES006 |  | DESK, cantilever, single pedestal 3 drawer, modesty panel, 1200W 750D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOI011 |  | HOIST, body handling, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LOC019 |  | LOCKER, 6 compartments, 1800H 300W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO263 |  | TROLLEY, mortuary, body transportation/weighing, stacking, manual/hydraulic, height adjustable | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1625 |  |  |  |  | Body store and handling area: 5 bays double ended, 25 bodies
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Receiving bodies on trolley. 2) Identify and label body, enter details in record book or computer. 3) Placing of shrouds on body. 4) Transfer of bodies to the refrigerated body store. 5) Holding of bodies in the refrigerated body store. 6) Removal of body from store to Bier room. 7) Removal of body from store for handing over to undertakers. 8) Computer workstation(s) may be used. 9) Parking hoist. 10) Equipment trolley(s) may be parked and/or stored. 11) Placing valuables in sealed container. 12) Clinical hand washing.
Personnel:
| Planning Relationships: | [5 empty] | Adjacent to Body Store. Adjacent to Bier room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 37 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Body store 4 bays 4 deg.C & 1 bay -20 deg.C. Bell push/two-way communication system linked from mortuary entrance - project team option. If bodies are to be prepared and/or undressed in the body handling area, there should be at least one screened bay to provide some privacy. Hoist, ceiling mounted - project team option. Refrigeration unit located in adjacent plant room. In Isolation section of mortuary design to take account of 'frost heave' precautions; 'anti-freeze' water mats at door seals; evaporator coil defrost requirements. Thermostatic control will be required for each compartment bay. Facilities should be provided to enable compartment bays not in use to be switched off. All socket outlets should be fed via a safe supply unit & be splash-proof - Ref. to text guide. For radioactive body handling & store requirements; ref. to Text Guide Appendix II. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
L1625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1625 |  |  |  |  | Body store and handling area: 5 bays double ended, 25 bodies
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN20
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200 |  | Suitable for use in low ambient temperatures
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1625 |  |  |  |  | Body store and handling area: 5 bays double ended, 25 bodies
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 1 x personnel access (900mm); 1 x personnel, trolley & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1625 |  |  |  |  | Body store and handling area: 5 bays double ended, 25 bodies
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BOD052 |  | BODY STORE, 4 deg.C, 3 - 5 tier adjustable, double ended, centre bay, lockable, nominal 2600H 800W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD053 |  | BODY STORE, 4 deg.C, 3 - 5 tier adjustable, double ended, right hand bay, lockable, nominal 2600H 900W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD056 |  | BODY STORE, 4 deg.C, extra wide, 3 - 5 tier adjustable, double ended, left hand bay, lockable, nominal 2600H 1100W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD061 |  | BODY STORE, -20 deg.C, 3 - 5 tier adjustable, double ended, lockable, nominal 2600H 1000W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL028 |  | BELL, call, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT032 |  | SOCKET outlet switched 13amp double, splashproof | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT351 |  | OUTLET, floor drainage and grating, 400W 400D, general pattern. HTM64FOG | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA037 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN003 |  | BIN, disposal, general purpose, liner, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA363 |  | CHAIR, height adjustable, with arms, high back, swivel, 5 star base, wipeable, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DES027 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1600W 800D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DES028 |  | DESK RETURN UNIT, cantilever, cable management, adjustable legs, modesty panel, freestanding, 1200W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOI011 |  | HOIST, body handling, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1625 |  |  |  |  | Body store and handling area: 5 bays double ended, 25 bodies
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 5 |  |  | 5 |  |  |  |  | LOC019 |  | LOCKER, 6 compartments, 1800H 300W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO263 |  | TROLLEY, mortuary, body transportation/weighing, stacking, manual/hydraulic, height adjustable | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1627
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1627 |  |  |  |  | Body store and handling area: 7 bays double ended, 35 bodies
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Receiving bodies on trolley. 2) Identify and label body, enter details in record book or computer. 3) Placing of shrouds on body. 4) Transfer of bodies to the refrigerated body store. 5) Holding of bodies in the refrigerated body store. 6) Removal of body from store to Bier room. 7) Removal of body from store for handing over to undertakers. 8) Computer workstation(s) may be used. 9) Parking hoist. 10) Equipment trolley(s) may be parked and/or stored. 11) Placing valuables in sealed container. 12) Clinical hand washing.
Personnel:
| Planning Relationships: | [5 empty] | Adjacent to Body Store. Adjacent to Bier room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 50 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Body store 6 bays 4 deg.C & 1 bay -20 deg.C. Bell push/two-way communication system linked from mortuary entrance - project team option. If bodies are to be prepared and/or undressed in the body handling area, there should be at least one screened bay to provide some privacy. Refrigeration unit located in adjacent plant room. In Isolation section of mortuary design to take account of 'frost heave' precautions; 'anti-freeze' water mats at door seals; evaporator coil defrost requirements. Thermostatic control will be required for each compartment bay. Facilities should be provided to enable compartment bays not in use to be switched off. All socket outlets should be fed via a safe supply unit & be splash-proof - Ref. to text guide. For radioactive body handling & store requirements; ref. to Text Guide Appendix II. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
L1627
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1627 |  |  |  |  | Body store and handling area: 7 bays double ended, 35 bodies
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN20
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200 |  | Suitable for use in low ambient temperatures
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1627
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1627 |  |  |  |  | Body store and handling area: 7 bays double ended, 35 bodies
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 1 x personnel, trolley & equipment access (1500mm) 1 x personnel, trolley & equipment access (1900mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1627
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1627 |  |  |  |  | Body store and handling area: 7 bays double ended, 35 bodies
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD051 |  | BODY STORE, 4 deg.C, 3 - 5 tier adjustable, double ended, left hand bay, lockable, nominal 2600H 900W 2400D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | BOD052 |  | BODY STORE, 4 deg.C, 3 - 5 tier adjustable, double ended, centre bay, lockable, nominal 2600H 800W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD053 |  | BODY STORE, 4 deg.C, 3 - 5 tier adjustable, double ended, right hand bay, lockable, nominal 2600H 900W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD056 |  | BODY STORE, 4 deg.C, extra wide, 3 - 5 tier adjustable, double ended, left hand bay, lockable, nominal 2600H 1100W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD061 |  | BODY STORE, -20 deg.C, 3 - 5 tier adjustable, double ended, lockable, nominal 2600H 1000W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL028 |  | BELL, call, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOI013 |  | HOIST, body handling, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT032 |  | SOCKET outlet switched 13amp double, splashproof | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT351 |  | OUTLET, floor drainage and grating, 400W 400D, general pattern. HTM64FOG | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA037 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN003 |  | BIN, disposal, general purpose, liner, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA363 |  | CHAIR, height adjustable, with arms, high back, swivel, 5 star base, wipeable, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DES027 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1600W 800D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DES028 |  | DESK RETURN UNIT, cantilever, cable management, adjustable legs, modesty panel, freestanding, 1200W 600D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1627
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1627 |  |  |  |  | Body store and handling area: 7 bays double ended, 35 bodies
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | LOC019 |  | LOCKER, 6 compartments, 1800H 300W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO263 |  | TROLLEY, mortuary, body transportation/weighing, stacking, manual/hydraulic, height adjustable | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1628
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1628 |  |  |  |  | Body store and handling area: 15 bays double ended, 75 bodies
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Receiving bodies on trolley. 2) Identify and label body, enter details in record book or computer. 3) Placing of shrouds on body. 4) Transfer of bodies to the refrigerated body store. 5) Holding of bodies in the refrigerated body store. 6) Removal of body from store to Bier room. 7) Removal of body from store for handing over to undertakers. 8) Computer workstation(s) may be used. 9) Parking hoist. 10) Equipment trolley(s) may be parked and/or stored. 11) Placing valuables in sealed container. 12) Clinical hand washing.
Personnel:
| Planning Relationships: | [5 empty] | Adjacent to Body Store. Adjacent to Bier room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 100 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Body store 14 bays 4 deg.C & 1 bay -20 deg.C. Bell push/two-way communication system linked from mortuary entrance - project team option. If bodies are to be prepared and/or undressed in the body handling area, there should be at least one screened bay to provide some privacy. Refrigeration unit located in adjacent plant room. In Isolation section of mortuary design to take account of 'frost heave' precautions; 'anti-freeze' water mats at door seals; evaporator coil defrost requirements. Thermostatic control will be required for each compartment bay. Facilities should be provided to enable compartment bays not in use to be switched off. All socket outlets should be fed via a safe supply unit & be splash-proof - Ref. to text guide. For radioactive body handling & store requirements; ref. to Text Guide Appendix II. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
L1628
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1628 |  |  |  |  | Body store and handling area: 15 bays double ended, 75 bodies
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN20
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200 |  | Suitable for use in low ambient temperatures
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1628
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1628 |  |  |  |  | Body store and handling area: 15 bays double ended, 75 bodies
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 1 x personnel, trolley & equipment access (1500mm) 1 x personnel, trolley & equipment access (1900mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1628
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1628 |  |  |  |  | Body store and handling area: 15 bays double ended, 75 bodies
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD051 |  | BODY STORE, 4 deg.C, 3 - 5 tier adjustable, double ended, left hand bay, lockable, nominal 2600H 900W 2400D | [16 empty] | 1
| 11 |  |  | 11 |  |  |  |  | BOD052 |  | BODY STORE, 4 deg.C, 3 - 5 tier adjustable, double ended, centre bay, lockable, nominal 2600H 800W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD053 |  | BODY STORE, 4 deg.C, 3 - 5 tier adjustable, double ended, right hand bay, lockable, nominal 2600H 900W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD056 |  | BODY STORE, 4 deg.C, extra wide, 3 - 5 tier adjustable, double ended, left hand bay, lockable, nominal 2600H 1100W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD061 |  | BODY STORE, -20 deg.C, 3 - 5 tier adjustable, double ended, lockable, nominal 2600H 1000W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL028 |  | BELL, call, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOI013 |  | HOIST, body handling, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT032 |  | SOCKET outlet switched 13amp double, splashproof | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT351 |  | OUTLET, floor drainage and grating, 400W 400D, general pattern. HTM64FOG | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA037 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN003 |  | BIN, disposal, general purpose, liner, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA363 |  | CHAIR, height adjustable, with arms, high back, swivel, 5 star base, wipeable, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DES027 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1600W 800D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DES028 |  | DESK RETURN UNIT, cantilever, cable management, adjustable legs, modesty panel, freestanding, 1200W 600D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1628
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1628 |  |  |  |  | Body store and handling area: 15 bays double ended, 75 bodies
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 13 |  |  | 13 |  |  |  |  | LOC019 |  | LOCKER, 6 compartments, 1800H 300W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO263 |  | TROLLEY, mortuary, body transportation/weighing, stacking, manual/hydraulic, height adjustable | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1629
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1629 |  |  |  |  | Body store and handling area: 20 bays double ended, 100 bodies
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Receiving bodies on trolley. 2) Identify and label body, enter details in record book or computer. 3) Placing of shrouds on body. 4) Transfer of bodies to the refrigerated body store. 5) Holding of bodies in the refrigerated body store. 6) Removal of body from store to Bier room. 7) Removal of body from store for handing over to undertakers. 8) Computer workstation(s) may be used. 9) Parking hoist. 10) Equipment trolley(s) may be parked and/or stored. 11) Placing valuables in sealed container. 12) Clinical hand washing.
Personnel:
| Planning Relationships: | [5 empty] | Adjacent to Body Store. Adjacent to Bier room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 125 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Body store 19 bays 4 deg.C & 1 bay -20 deg.C. Bell push/two-way communication system linked from mortuary entrance - project team option. If bodies are to be prepared and/or undressed in the body handling area, there should be at least one screened bay to provide some privacy. Refrigeration unit located in adjacent plant room. In Isolation section of mortuary design to take account of 'frost heave' precautions; 'anti-freeze' water mats at door seals; evaporator coil defrost requirements. Thermostatic control will be required for each compartment bay. Facilities should be provided to enable compartment bays not in use to be switched off. All socket outlets should be fed via a safe supply unit & be splash-proof - Ref. to text guide. For radioactive body handling & store requirements; ref. to Text Guide Appendix II. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
L1629
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1629 |  |  |  |  | Body store and handling area: 20 bays double ended, 100 bodies
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN20
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200 |  | Suitable for use in low ambient temperatures
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1629
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1629 |  |  |  |  | Body store and handling area: 20 bays double ended, 100 bodies
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 1 x personnel, trolley & equipment access (1500mm) 1 x personnel, trolley & equipment access (1900mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1629
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1629 |  |  |  |  | Body store and handling area: 20 bays double ended, 100 bodies
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD051 |  | BODY STORE, 4 deg.C, 3 - 5 tier adjustable, double ended, left hand bay, lockable, nominal 2600H 900W 2400D | [16 empty] | 1
| 16 |  |  | 16 |  |  |  |  | BOD052 |  | BODY STORE, 4 deg.C, 3 - 5 tier adjustable, double ended, centre bay, lockable, nominal 2600H 800W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD053 |  | BODY STORE, 4 deg.C, 3 - 5 tier adjustable, double ended, right hand bay, lockable, nominal 2600H 900W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD056 |  | BODY STORE, 4 deg.C, extra wide, 3 - 5 tier adjustable, double ended, left hand bay, lockable, nominal 2600H 1100W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD061 |  | BODY STORE, -20 deg.C, 3 - 5 tier adjustable, double ended, lockable, nominal 2600H 1000W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL028 |  | BELL, call, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOI013 |  | HOIST, body handling, ceiling mounted | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT032 |  | SOCKET outlet switched 13amp double, splashproof | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT351 |  | OUTLET, floor drainage and grating, 400W 400D, general pattern. HTM64FOG | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA037 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN003 |  | BIN, disposal, general purpose, liner, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA363 |  | CHAIR, height adjustable, with arms, high back, swivel, 5 star base, wipeable, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DES027 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1600W 800D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DES028 |  | DESK RETURN UNIT, cantilever, cable management, adjustable legs, modesty panel, freestanding, 1200W 600D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1629
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1629 |  |  |  |  | Body store and handling area: 20 bays double ended, 100 bodies
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 17 |  |  | 17 |  |  |  |  | LOC019 |  | LOCKER, 6 compartments, 1800H 300W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO263 |  | TROLLEY, mortuary, body transportation/weighing, stacking, manual/hydraulic, height adjustable | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1641
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1641 |  |  |  |  | Post-mortem room: 1 table, special procedures
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Body on trolley brought from body store. 2) Body transferred to table. 3) External and internal examination of body by pathologist. 4) Pathologist/technician opens body. 5) Pathologist dictates body description and findings for recording. 6) Organs removed and transferred to cutting-up bench or board fitted across foot-end of table. 7) Weighing organs on cutting-up bench. 8) Dissecting, weighing, describing and recording of organs. 9) Organs retained for investigation placed in container/s. 10) Retained specimens transferred to room or direct to Histopathology Dept. 11) Remaining organs returned to body. 12) Viewing and recording of post-mortems by medical observers. 13) Body reconstituted, washed wrapped in shroud and returned to refrigerator. 14) Emergency eye irrigation following contamination with corrosive or irritant substances.
| Personnel: | [6 empty] | Intermittent use
| Planning Relationships: | [5 empty] | Access via main PM room & Transit area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 27 |  |  |  |  | Height (mm): |  |  |  | 3000
| Notes: | [7 empty] | Suitable for the coroner or forensic pathologist for major forensic work e.g. in case of suspected homicide - project team option. Ventilated tables - project team option. All socket outlets should be fed via a safe supply unit & be splash-proof - Ref. to text guide. Pendant gimbals type to be fed from safe supply unit - Ref. to text guide. Exhaust separately to outside of building - Ref. to text guide. Occasional use of imaging x-ray equipment. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
L1641
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1641 |  |  |  |  | Post-mortem room: 1 table, special procedures
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN20. Clean air path required. Discharge from extract system may be contaminated and should be sited accordingly. Seek specialist guidance if High Risk infectious cases are to be handled.
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1641
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1641 |  |  |  |  | Post-mortem room: 1 table, special procedures
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 1 x personnel access (900mm); 1 x personnel, trolley & equipment access (1900mm)
| Windows: | [5 empty] | Desirable - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Essential To observation area where provided (see A Sheet for room L1602) Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1641
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1641 |  |  |  |  | Post-mortem room: 1 table, special procedures
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | DIC010 |  | DICTATION POINT adjustable microphone, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIC012 |  | DICTATION POINT, ceiling-cord suspended | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU013 |  | DISPOSAL UNIT, hopper with flushing rim, 110mm outlet, no tap holes no overflow, back inlet, stainless steel, 900H 600W 600D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG053 |  | LUMINAIRE, examination, ceiling, adjustable, 1000 lux | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT030 |  | SOCKET outlet switched 13amp single, splashproof | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT032 |  | SOCKET outlet switched 13amp double, splashproof | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT115 |  | SOCKET outlet dictaphone. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT116 |  | SOCKET outlet dictaphone, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT351 |  | OUTLET, floor drainage and grating, 400W 400D, general pattern. HTM64FOG | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | PEN010 |  | PENDANT power supply unit, outlets: 2x 13amp switched, double, flexible unit, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SIN079 |  | SINK stainless steel, 450mm deep, on leg supports, 900H 600W 650D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SIN095 |  | SINK/BENCH UNIT, dissecting, ventilated stainless steel drain, lipped front, integral continuous back upstand, hose and water supply | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SWC080 |  | SWITCH dictaphone/microphone flush, floor mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAB080 |  | TABLE, post mortem, stainless steel, drain, 915H 610W 2057D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP001 |  | TAP extension piece(bib/pillar), length to suit | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP894 |  | TAP bib, hospital pattern, integral thermostatic mixer, automatic action with sensor operation. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TRO601 |  | TROUGH scrub-up, hospital pattern, stainless steel, single, 75mm upstand, 800W 450D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WKT409 |  | WORKTOP, plain, stainless steel, cantilevered from wall, 1500W 550D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOT001 |  | BOTTLE, eye irrigation, emergency, with internal application, fix panel | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS008 |  | DISPENSER, nailbrush, autoclavable, stainless steel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS025 |  | DISPENSER, soap, foot operated, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA201 |  | BOARD, dissecting processed rubber, 100H 550W 350D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1641
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1641 |  |  |  |  | Post-mortem room: 1 table, special procedures
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BOA202 |  | BOARD, dissecting, polypropylene, 300H 800W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1642
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1642 |  |  |  |  | Post-mortem room: 2 tables Access to body store 5 bays
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Transfer body from body store to a table. 2) External and internal examination of body by pathologist. 3) Pathologist/technician opens body. 4) Pathologist dictates body description and findings for recording. 5) Organs removed and transferred to cutting-up bench or board fitted across foot-end of table. 6) Weighing organs on cutting-up bench. 7) Dissecting, weighing, describing and recording of organs. 8) Organs retained for investigation placed in container/s. 9) Retained specimens transferred to room or direct to Histopathology Dept. 10) Remaining organs returned to body. 11) Viewing and recording of post-mortems by medical observers. 12) Body reconstituted, washed wrapped in shroud and returned to refrigerator. 13) Emergency eye irrigation following contamination with corrosive or irritant substances.
| Personnel: | [6 empty] | Intermittent use
| Planning Relationships: | [5 empty] | Direct access to body store 5 bays. Adjacent to dirty utility room/area. Adjacent to transit area/staff changing.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 70 |  |  |  |  | Height (mm): |  |  |  | 3000
| Notes: | [7 empty] | Ventilated tables - project team option. All socket outlets should be fed via a safe supply unit & be splash-proof - Ref. to text guide. Pendant gimbals type to be fed from safe supply unit - Ref. to text guide. Exhaust separately to outside of building - Ref. to text guide. Occasional use of imaging x-ray equipment. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
L1642
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1642 |  |  |  |  | Post-mortem room: 2 tables Access to body store 5 bays
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN20. Clean air path required. Discharge from extract system may be contaminated and should be sited accordingly. Seek specialist guidance if High Risk infectious cases are to be handled.
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1642
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1642 |  |  |  |  | Post-mortem room: 2 tables Access to body store 5 bays
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm)
| Windows: | [5 empty] | Desirable - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Essential To observation area where provided (see A Sheet for room L1602) Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1642
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1642 |  |  |  |  | Post-mortem room: 2 tables Access to body store 5 bays
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | DIC010 |  | DICTATION POINT adjustable microphone, wall mounted | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | DIC012 |  | DICTATION POINT, ceiling-cord suspended | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU013 |  | DISPOSAL UNIT, hopper with flushing rim, 110mm outlet, no tap holes no overflow, back inlet, stainless steel, 900H 600W 600D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LIG053 |  | LUMINAIRE, examination, ceiling, adjustable, 1000 lux | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT030 |  | SOCKET outlet switched 13amp single, splashproof | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT032 |  | SOCKET outlet switched 13amp double, splashproof | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT115 |  | SOCKET outlet dictaphone. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT116 |  | SOCKET outlet dictaphone, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT351 |  | OUTLET, floor drainage and grating, 400W 400D, general pattern. HTM64FOG | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | PEN010 |  | PENDANT power supply unit, outlets: 2x 13amp switched, double, flexible unit, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SIN079 |  | SINK stainless steel, 450mm deep, on leg supports, 900H 600W 650D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SIN095 |  | SINK/BENCH UNIT, dissecting, ventilated stainless steel drain, lipped front, integral continuous back upstand, hose and water supply | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SWC080 |  | SWITCH dictaphone/microphone flush, floor mounted | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAB080 |  | TABLE, post mortem, stainless steel, drain, 915H 610W 2057D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP001 |  | TAP extension piece(bib/pillar), length to suit | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | TAP894 |  | TAP bib, hospital pattern, integral thermostatic mixer, automatic action with sensor operation. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TRO601 |  | TROUGH scrub-up, hospital pattern, stainless steel, single, 75mm upstand, 800W 450D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WKT409 |  | WORKTOP, plain, stainless steel, cantilevered from wall, 1500W 550D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOT001 |  | BOTTLE, eye irrigation, emergency, with internal application, fix panel | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS025 |  | DISPENSER, soap, foot operated, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | BOA201 |  | BOARD, dissecting processed rubber, 100H 550W 350D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | BOA202 |  | BOARD, dissecting, polypropylene, 300H 800W 300D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1642
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1642 |  |  |  |  | Post-mortem room: 2 tables Access to body store 5 bays
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOI011 |  | HOIST, body handling, mobile | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO264 |  | TROLLEY, mortuary, body transportation, stacking, manual/hydraulic, height adjustable | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1643
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1643 |  |  |  |  | Post-mortem room: 2 tables Access to body store 7 bays
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Transfer body from body store to a table. 2) External and internal examination of body by pathologist. 3) Pathologist/technician opens body. 4) Pathologist dictates body description and findings for recording. 5) Organs removed and transferred to cutting-up bench or board fitted across foot-end of table. 6) Weighing organs on cutting-up bench. 7) Dissecting, weighing, describing and recording of organs. 8) Organs retained for investigation placed in container/s. 9) Retained specimens transferred to room or direct to Histopathology Dept. 10) Remaining organs returned to body. 11) Viewing and recording of post-mortems by medical observers. 12) Body reconstituted, washed wrapped in shroud and returned to refrigerator. 13) Emergency eye irrigation following contamination with corrosive or irritant substances.
| Personnel: | [6 empty] | Intermittent use
| Planning Relationships: | [5 empty] | Direct access to body store 7 bays. Adjacent to dirty utility room/area. Adjacent to transit area/staff changing.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 75 |  |  |  |  | Height (mm): |  |  |  | 3000
| Notes: | [7 empty] | Ventilated tables - project team option. All socket outlets should be fed via a safe supply unit & be splash-proof - Ref. to text guide. Pendant gimbals type to be fed from safe supply unit - Ref. to text guide. Exhaust separately to outside of building - Ref. to text guide. Occasional use of imaging x-ray equipment. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
L1643
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1643 |  |  |  |  | Post-mortem room: 2 tables Access to body store 7 bays
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN20. Clean air path required. Discharge from extract system may be contaminated and should be sited accordingly. Seek specialist guidance if High Risk infectious cases are to be handled.
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1643
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1643 |  |  |  |  | Post-mortem room: 2 tables Access to body store 7 bays
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm)
| Windows: | [5 empty] | Desirable - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Essential To observation area where provided (see A Sheet for room L1602) Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1643
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1643 |  |  |  |  | Post-mortem room: 2 tables Access to body store 7 bays
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | DIC010 |  | DICTATION POINT adjustable microphone, wall mounted | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | DIC012 |  | DICTATION POINT, ceiling-cord suspended | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU013 |  | DISPOSAL UNIT, hopper with flushing rim, 110mm outlet, no tap holes no overflow, back inlet, stainless steel, 900H 600W 600D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LIG053 |  | LUMINAIRE, examination, ceiling, adjustable, 1000 lux | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT030 |  | SOCKET outlet switched 13amp single, splashproof | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT032 |  | SOCKET outlet switched 13amp double, splashproof | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT115 |  | SOCKET outlet dictaphone. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT116 |  | SOCKET outlet dictaphone, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT351 |  | OUTLET, floor drainage and grating, 400W 400D, general pattern. HTM64FOG | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | PEN010 |  | PENDANT power supply unit, outlets: 2x 13amp switched, double, flexible unit, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SIN079 |  | SINK stainless steel, 450mm deep, on leg supports, 900H 600W 650D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SIN095 |  | SINK/BENCH UNIT, dissecting, ventilated stainless steel drain, lipped front, integral continuous back upstand, hose and water supply | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SWC080 |  | SWITCH dictaphone/microphone flush, floor mounted | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAB080 |  | TABLE, post mortem, stainless steel, drain, 915H 610W 2057D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP001 |  | TAP extension piece(bib/pillar), length to suit | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | TAP894 |  | TAP bib, hospital pattern, integral thermostatic mixer, automatic action with sensor operation. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TRO601 |  | TROUGH scrub-up, hospital pattern, stainless steel, single, 75mm upstand, 800W 450D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WKT409 |  | WORKTOP, plain, stainless steel, cantilevered from wall, 1500W 550D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOT001 |  | BOTTLE, eye irrigation, emergency, with internal application, fix panel | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS025 |  | DISPENSER, soap, foot operated, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | BOA201 |  | BOARD, dissecting processed rubber, 100H 550W 350D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | BOA202 |  | BOARD, dissecting, polypropylene, 300H 800W 300D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1643
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1643 |  |  |  |  | Post-mortem room: 2 tables Access to body store 7 bays
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOI011 |  | HOIST, body handling, mobile | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO264 |  | TROLLEY, mortuary, body transportation, stacking, manual/hydraulic, height adjustable | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1645
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1645 |  |  |  |  | Post-mortem room: 3 tables Access to body store 15 bays
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Transfer body from body store to a table. 2) External and internal examination of body by pathologist. 3) Pathologist/technician opens body. 4) Pathologist dictates body description and findings for recording. 5) Organs removed and transferred to cutting-up bench or board fitted across foot-end of table. 6) Weighing organs on cutting-up bench. 7) Dissecting, weighing, describing and recording of organs. 8) Organs retained for investigation placed in container/s. 9) Retained specimens transferred to room or direct to Histopathology Dept. 10) Remaining organs returned to body. 11) Viewing and recording of post-mortems by medical observers. 12) Body reconstituted, washed wrapped in shroud and returned to refrigerator. 13) Emergency eye irrigation following contamination with corrosive or irritant substances.
| Personnel: | [6 empty] | Intermittent use
| Planning Relationships: | [5 empty] | Direct access to body store 15 bays. Adjacent to dirty utility room/area. Adjacent to transit area/staff changing.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 102 |  |  |  |  | Height (mm): |  |  |  | 3000
| Notes: | [7 empty] | Ventilated tables - project team option. All socket outlets should be fed via a safe supply unit & be splash-proof - Ref. to text guide. Pendant gimbals type to be fed from safe supply unit - Ref. to text guide. Exhaust separately to outside of building - Ref. to text guide. Occasional use of imaging x-ray equipment. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
L1645
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1645 |  |  |  |  | Post-mortem room: 3 tables Access to body store 15 bays
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN20. Clean air path required. Discharge from extract system may be contaminated and should be sited accordingly. Seek specialist guidance if High Risk infectious cases are to be handled.
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1645
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1645 |  |  |  |  | Post-mortem room: 3 tables Access to body store 15 bays
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm)
| Windows: | [5 empty] | Desirable - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Essential To observation area where provided (see A Sheet for room L1602) Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1645
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1645 |  |  |  |  | Post-mortem room: 3 tables Access to body store 15 bays
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | DIC010 |  | DICTATION POINT adjustable microphone, wall mounted | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | DIC012 |  | DICTATION POINT, ceiling-cord suspended | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU013 |  | DISPOSAL UNIT, hopper with flushing rim, 110mm outlet, no tap holes no overflow, back inlet, stainless steel, 900H 600W 600D. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | LIG053 |  | LUMINAIRE, examination, ceiling, adjustable, 1000 lux | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT030 |  | SOCKET outlet switched 13amp single, splashproof | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT032 |  | SOCKET outlet switched 13amp double, splashproof | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT115 |  | SOCKET outlet dictaphone. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT116 |  | SOCKET outlet dictaphone, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT351 |  | OUTLET, floor drainage and grating, 400W 400D, general pattern. HTM64FOG | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | PEN010 |  | PENDANT power supply unit, outlets: 2x 13amp switched, double, flexible unit, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SIN079 |  | SINK stainless steel, 450mm deep, on leg supports, 900H 600W 650D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SIN095 |  | SINK/BENCH UNIT, dissecting, ventilated stainless steel drain, lipped front, integral continuous back upstand, hose and water supply | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | SWC080 |  | SWITCH dictaphone/microphone flush, floor mounted | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | TAB080 |  | TABLE, post mortem, stainless steel, drain, 915H 610W 2057D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP001 |  | TAP extension piece(bib/pillar), length to suit | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | TAP894 |  | TAP bib, hospital pattern, integral thermostatic mixer, automatic action with sensor operation. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TRO601 |  | TROUGH scrub-up, hospital pattern, stainless steel, single, 75mm upstand, 800W 450D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WKT409 |  | WORKTOP, plain, stainless steel, cantilevered from wall, 1500W 550D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOT001 |  | BOTTLE, eye irrigation, emergency, with internal application, fix panel | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS025 |  | DISPENSER, soap, foot operated, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | BOA201 |  | BOARD, dissecting processed rubber, 100H 550W 350D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | BOA202 |  | BOARD, dissecting, polypropylene, 300H 800W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1645
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1645 |  |  |  |  | Post-mortem room: 3 tables Access to body store 15 bays
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOI011 |  | HOIST, body handling, mobile | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO264 |  | TROLLEY, mortuary, body transportation, stacking, manual/hydraulic, height adjustable | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1647
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1647 |  |  |  |  | Post-mortem room: 4 tables Access to body store 20 bays
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Transfer body from body store to a table. 2) External and internal examination of body by pathologist. 3) Pathologist/technician opens body. 4) Pathologist dictates body description and findings for recording. 5) Organs removed and transferred to cutting-up bench or board fitted across foot-end of table. 6) Weighing organs on cutting-up bench. 7) Dissecting, weighing, describing and recording of organs. 8) Organs retained for investigation placed in container/s. 9) Retained specimens transferred to room or direct to Histopathology Dept. 10) Remaining organs returned to body. 11) Viewing and recording of post-mortems by medical observers. 12) Body reconstituted, washed wrapped in shroud and returned to refrigerator. 13) Emergency eye irrigation following contamination with corrosive or irritant substances.
| Personnel: | [6 empty] | Intermittent use
| Planning Relationships: | [5 empty] | Direct access to body store 20 bays. Adjacent to dirty utility room/area. Adjacent to transit area/staff changing.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 135 |  |  |  |  | Height (mm): |  |  |  | 3000
| Notes: | [7 empty] | Ventilated tables - project team option. All socket outlets should be fed via a safe supply unit & be splash-proof - Ref. to text guide. Pendant gimbals type to be fed from safe supply unit - Ref. to text guide. Exhaust separately to outside of building - Ref. to text guide. Occasional use of imaging x-ray equipment. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
L1647
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1647 |  |  |  |  | Post-mortem room: 4 tables Access to body store 20 bays
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 15
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN20. Clean air path required. Discharge from extract system may be contaminated and should be sited accordingly. Seek specialist guidance if High Risk infectious cases are to be handled.
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1647
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1647 |  |  |  |  | Post-mortem room: 4 tables Access to body store 20 bays
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm)
| Windows: | [5 empty] | Desirable - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Essential To observation area where provided (see A Sheet for room L1602) Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1647
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1647 |  |  |  |  | Post-mortem room: 4 tables Access to body store 20 bays
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | DIC010 |  | DICTATION POINT adjustable microphone, wall mounted | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | DIC012 |  | DICTATION POINT, ceiling-cord suspended | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU013 |  | DISPOSAL UNIT, hopper with flushing rim, 110mm outlet, no tap holes no overflow, back inlet, stainless steel, 900H 600W 600D. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | LIG053 |  | LUMINAIRE, examination, ceiling, adjustable, 1000 lux | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT030 |  | SOCKET outlet switched 13amp single, splashproof | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT032 |  | SOCKET outlet switched 13amp double, splashproof | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT115 |  | SOCKET outlet dictaphone. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT116 |  | SOCKET outlet dictaphone, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT351 |  | OUTLET, floor drainage and grating, 400W 400D, general pattern. HTM64FOG | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | PEN010 |  | PENDANT power supply unit, outlets: 2x 13amp switched, double, flexible unit, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SIN079 |  | SINK stainless steel, 450mm deep, on leg supports, 900H 600W 650D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SIN095 |  | SINK/BENCH UNIT, dissecting, ventilated stainless steel drain, lipped front, integral continuous back upstand, hose and water supply | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | SWC080 |  | SWITCH dictaphone/microphone flush, floor mounted | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | TAB080 |  | TABLE, post mortem, stainless steel, drain, 915H 610W 2057D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP001 |  | TAP extension piece(bib/pillar), length to suit | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | TAP894 |  | TAP bib, hospital pattern, integral thermostatic mixer, automatic action with sensor operation. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TRO601 |  | TROUGH scrub-up, hospital pattern, stainless steel, single, 75mm upstand, 800W 450D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WKT409 |  | WORKTOP, plain, stainless steel, cantilevered from wall, 1500W 550D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOT001 |  | BOTTLE, eye irrigation, emergency, with internal application, fix panel | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS025 |  | DISPENSER, soap, foot operated, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | BOA201 |  | BOARD, dissecting processed rubber, 100H 550W 350D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | BOA202 |  | BOARD, dissecting, polypropylene, 300H 800W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1647
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1647 |  |  |  |  | Post-mortem room: 4 tables Access to body store 20 bays
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOI011 |  | HOIST, body handling, mobile | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO264 |  | TROLLEY, mortuary, body transportation, stacking, manual/hydraulic, height adjustable | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1651
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1651 |  |  |  |  | Temporary body store building (portable): 5 bays, 25 bodies Mortuary
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Receiving bodies on trolley. 2) Identify and label body, enter details in record book or computer. 3) Placing of shrouds on body. 4) Transfer of bodies to the refrigerated body store. 5) Holding of bodies in the refrigerated body store. 6) Removal of body from store for handing over to undertakers. 7) Equipment trolley(s) may be parked and/or stored. 8) Clinical hand washing.
Personnel:
| Planning Relationships: | [5 empty] | External standing space.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 29 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Standard portable building requiring external standing space & service connections. For temporary body stores details ref. to text guide Appendix IV. All socket outlets should be fed via a safe supply unit & be splash-proof - Ref. to text guide. Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
L1651
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1651 |  |  |  |  | Temporary body store building (portable): 5 bays, 25 bodies Mortuary
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
Permissible Space Temerature Range(dry bulb) (degC):
Heating Design Temperature (dry bulb)(degC):
Minimum Air Changes (AC/hr):
Ventilation Type:
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
Supply Air: Final Filter Class
Permisiible Relative Humidity Range (%):
| General Notes: | [5 empty] | Refer to HBN20
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200 |  | Suitable for use in low ambient temperatures
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Medium |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1651
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1651 |  |  |  |  | Temporary body store building (portable): 5 bays, 25 bodies Mortuary
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley & equipment access (1900mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1651
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | L1651 |  |  |  |  | Temporary body store building (portable): 5 bays, 25 bodies Mortuary
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD031 |  | BODY STORE, 4 deg.C, 3 - 5 tier adjustable, single ended, left hand bay, lockable, nominal 2600H 900W 2400D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | BOD032 |  | BODY STORE, 4 deg.C, 3 - 5 tier adjustable, single ended, centre bay, lockable, nominal 2600H 800W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOD033 |  | BODY STORE, 4 deg.C, 3 - 5 tier adjustable, single ended, right hand bay, lockable, nominal 2600H 900W 2400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU013 |  | DISPOSAL UNIT, hopper with flushing rim, 110mm outlet, no tap holes no overflow, back inlet, stainless steel, 900H 600W 600D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT030 |  | SOCKET outlet switched 13amp single, splashproof | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT032 |  | SOCKET outlet switched 13amp double, splashproof | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP001 |  | TAP extension piece(bib/pillar), length to suit | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WKT409 |  | WORKTOP, plain, stainless steel, cantilevered from wall, 1500W 550D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 5 |  |  | 5 |  |  |  |  | LOC019 |  | LOCKER, 6 compartments, 1800H 300W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO263 |  | TROLLEY, mortuary, body transportation/weighing, stacking, manual/hydraulic, height adjustable | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Clinical administration. 2) Computer workstation(s) may be used. 3) Telephone(s) may be used. 4) Discussions and interviews may take place. 5) Files and records are stored. 6) Hanging outdoor clothing. 7) Secure holding/storing of clothing and personal belongings. 8) Printer may be used. 9) Electronic patient records (EPRs) may be accessed and updated. 10) Staff notices, information and/or messages may be displayed. 11) Dealing with enquiries. 12) Information on computers may be accessed.
| Personnel: | [6 empty] | 1 x staff Up to x 2 others.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following equipment is shown on the room layout but is optional: - call repeat lamps for controlled drugs cupboards (but required if the office is used for clinical control). The following items may provided; - shelving; - printer. The following items may be provided if the office is used for clinical control: - a small safe; - a key cupboard; - an alarm panel, see HTM 08-03; - a dimming switch - recommended if the room is used for viewing digital images. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 3 |  |  | 3 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG138 |  | LUMINAIRE, indicating controlled drugs cupboard repeat | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB049 |  | CABINET, lateral filing, 6 rails, 2 door, 1970H 1000W 470D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DES026 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1400W 700D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA057 |  | DRAWER UNIT, 3 drawer, lockable, on castors, desk height 715H 430W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0252
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | M0252 |  |  |  |  | Office: 2 person
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Clinical administration. 2) Computer workstation(s) may be used. 3) Telephone(s) may be used. 4) Discussions and interviews may take place. 5) Files and records are stored. 6) Hanging outdoor clothing. 7) Staff notices, information and/or messages may be displayed. 8) Printer may be used. 9) Dealing with enquiries. 10) Information on computers may be accessed.
| Personnel: | [6 empty] | 2 x staff. Up to 2 x others.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following equipment is shown on the room layout but is optional: - call repeat lamps for controlled drugs cupboards (but required if the office is used for clinical control). The following items may be provided if the office is used for clinical control: - a dimming switch - recommended if the room is used for viewing digital images. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0252
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | M0252 |  |  |  |  | Office: 2 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0252
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | M0252 |  |  |  |  | Office: 2 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0252
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | M0252 |  |  |  |  | Office: 2 person
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 3 |  |  | 3 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG138 |  | LUMINAIRE, indicating controlled drugs cupboard repeat | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB049 |  | CABINET, lateral filing, 6 rails, 2 door, 1970H 1000W 470D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | DES026 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1400W 700D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | DRA057 |  | DRAWER UNIT, 3 drawer, lockable, on castors, desk height 715H 430W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0724
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | M0724 |  |  |  |  | Interview room: 4 places (including 1 wheelchair place)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Discussions and interviews may take place. 2) Telephone(s) may be used. 3) Laptop computer(s) may be used. 4) Call systems may be used.
| Personnel: | [6 empty] | Up to 4 x persons.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items are shown on the room layout but are optional: - staff emergency call (not required if the room is for staff use only); - telephone (should not be provided in rooms intended as quiet spaces); - room in use switch and indicator. The following items may be provided: - a clinical wash-hand basin and gel dispenser to allow for clinical use of the room; . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0724
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | M0724 |  |  |  |  | Interview room: 4 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0724
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | M0724 |  |  |  |  | Interview room: 4 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0724
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | M0724 |  |  |  |  | Interview room: 4 places (including 1 wheelchair place)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG073 |  | ILLUMINATED SIGN, 'Room in use' | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC076 |  | SWITCH, 'Room in use' illuminated sign. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | P0711
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | P0711 |  |  |  |  | Mini kitchen
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Microwave oven may be used. 2) Provision of refrigerated storage. 3) Small amounts of dry goods are stored in cupboard(s). 4) Disposal of waste and contaminated materials. 5) Hand-rinse basin may be used. 6) People preparing beverages, meals and snacks.
| Personnel: | [6 empty] | 1 - 2 x persons. Intermittent use.
| Planning Relationships: | [5 empty] | Integral part of another space, usually a staff rest room
| Space Data: | [6 empty] | Area (m²): |  |  |  | 5 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
| Notes: | [7 empty] | The following items are included on the room layout but are optional: - a microwave oven. The layout is suitable for ambulant/semi-ambulant users, consideration must be given to wheelchair user provision.
| ADB | [7 empty] | Room Environmental Data
P0711
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | P0711 |  |  |  |  | Mini kitchen
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | -
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Heat
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | P0711
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | P0711 |  |  |  |  | Mini kitchen
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | P0711
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | P0711 |  |  |  |  | Mini kitchen
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP715 |  | CUPBOARD, base, including sink panel, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP731 |  | CUPBOARD/DRAWER UNIT, base, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT301 |  | OUTLET, cold water for equipment | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP359 |  | TAP, pillar, high neck, long lever, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAT003 |  | WATER BOILER, 2.5 litre, electric, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WRT221 |  | WORKTOP, dished, stainless steel, with integral centre sink bowl and 2 tap holes, 2100W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP252 |  | CUPBOARD, 2 adjustable shelves, wall mounted, 750H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP259 |  | CUPBOARD, space for built in microwave, wall mounted, 750H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | OVE016 |  | OVEN, microwave, capacity 18 litre, build in, (suitable for CUP259) | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF058 |  | REFRIGERATOR, capacity 160 litre, automatic defrost, stainless steel, underbench, external temperature gauge, lockable, on castors, 850H 610W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | S0028
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | S0028 |  |  |  |  | Counselling room with beverage bay: 8 person Family
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Distressed relatives to wait in privacy. 2) Confidential and informal discussions and advising relatives. 3) Comforting relatives/carers. 4) People preparing beverages, meals and snacks. 5) Occasional consumption of beverages. 6) Telephone(s) may be used.
| Personnel: | [6 empty] | 1 x Staff Up to 7 others, including wheelchair person.
| Planning Relationships: | [5 empty] | Close to patient areas. Close to staff work areas. Sanitary facilities en-suite/or conveniently located - project option.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 16 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
S0028
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | S0028 |  |  |  |  | Counselling room with beverage bay: 8 person Family
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Confidential |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | S0028
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | S0028 |  |  |  |  | Counselling room with beverage bay: 8 person Family
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control. Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | S0028
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | S0028 |  |  |  |  | Counselling room with beverage bay: 8 person Family
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAT003 |  | MINI KITCHEN (combined unit) with refrigerator, sink top, wall cabinet, cupboard and drawers, laminate backboard, 1970H 1200W 600D | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC073 |  | CABINET, upper, modular storage, for 600 facing inserts, with door, 750H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAT003 |  | WATER BOILER, 2.5 litre, electric, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CHA378 |  | UNIT CHAIR, easy, with arms, fully upholstered, wipeable, | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA379 |  | UNIT CHAIR/SETTEE, 2 seater, easy, with arms, fully upholstered, wipeable. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA380 |  | UNIT CHAIR/SETTEE, 3 seater, easy, with arms, fully upholstered, wipeable. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0554-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V0554-01 |  |  |  |  | Staff communal changing room: 5 lockers
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) User may undress and dress. 2) Changing into clean uniforms (including blues or greens). 3) Changing footwear. 4) Secure hanging of wet outdoor clothing. 5) Secure holding/storing of clothing and personal belongings. 6) Secure holding/storage of motorcycle and bicycle helmets. 7) Hanging outdoor clothing. 8) Disposal of dirty uniforms.
| Personnel: | [6 empty] | Up to 3 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Direct access to showers and/or individual changing room(s). Close to WCs. Close to uniform exchange, if provided.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | It is assumed that this space is supported by one individual changing room. See V0725 for details of semi-ambulant individual changing room and V0276 for independent wheelchair individual changing room. The room layout illustrates space for all users but includes lockers for generally ambulant users. A suitable number of lockers must comply with the requirements of BS8300/ADM for wheelchair users depending upon the expected user group. The following items may be provided: - cube lockers for personal belongings will be required if staff are not allocated their own changing lockers; - shaver sockets, shelves and lights associated with mirrors.
| ADB | [7 empty] | Room Environmental Data
V0554-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V0554-01 |  |  |  |  | Staff communal changing room: 5 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0554-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V0554-01 |  |  |  |  | Staff communal changing room: 5 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0554-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V0554-01 |  |  |  |  | Staff communal changing room: 5 lockers
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CHA383 |  | CHAIR, stacking, polypropylene, with back and seat pads, wipeable. | [16 empty] | 3
| 5 |  |  | 5 |  |  |  |  | LOC005 |  | LOCKER clothes, single, 1800H 300W 550D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC158 |  | RACK shoe, (bridge unit base between lockers assembly) 175H 600W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAI026 |  | RAIL, coat hanging, 10 secure hangers with sleeve lock chain, (bridge unit top between lockers assembly), 600L | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0554-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V0554-02 |  |  |  |  | Staff communal changing room: 10 lockers
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) User may undress and dress. 2) Changing into clean uniforms (including blues or greens). 3) Changing footwear. 4) Secure hanging of wet outdoor clothing. 5) Secure holding/storing of clothing and personal belongings. 6) Secure holding/storage of motorcycle and bicycle helmets. 7) Hanging outdoor clothing. 8) Disposal of dirty uniforms.
| Personnel: | [6 empty] | Up to 4 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Direct access to showers and/or individual changing room(s). Close to WCs. Close to uniform exchange, if provided.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 11 |  |  |  |  | Height (mm): |  |  |  | 2700
.
| Notes: | [7 empty] | It is assumed that this space is supported by one individual changing room. See V0725 for details of semi-ambulant individual changing room and V0276 for independent wheelchair individual changing room. The room layout illustrates space for all users but includes lockers for generally ambulant users. A suitable number of lockers must comply with the requirements of BS8300/ADM for wheelchair users depending upon the expected user group. The following items may be provided: - cube lockers for personal belongings will be required if staff are not allocated their own changing lockers; - shaver sockets, shelves and lights associated with mirrors.
| ADB | [7 empty] | Room Environmental Data
V0554-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V0554-02 |  |  |  |  | Staff communal changing room: 10 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0554-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V0554-02 |  |  |  |  | Staff communal changing room: 10 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0554-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V0554-02 |  |  |  |  | Staff communal changing room: 10 lockers
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CHA383 |  | CHAIR, stacking, polypropylene, with back and seat pads, wipeable. | [16 empty] | 3
| 10 |  |  | 10 |  |  |  |  | LOC005 |  | LOCKER clothes, single, 1800H 300W 550D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC154 |  | RACK shoe, (bridge unit base between lockers assembly) 175H 1200W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAI023 |  | RAIL, coat hanging, 20 secure hangers with sleeve lock chain, (bridge unit top between lockers assembly), 1200W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Semi-ambulant person may undress/dress in privacy. 2) Hanging outdoor clothing. 3) Call systems may be used.
| Personnel: | [6 empty] | 1 x person. Intermittent use.
| Planning Relationships: | [5 empty] | Adjacent to sub-waiting area (if provided). Close to WC facilities. May be use in conjunction with staff changing area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items are shown on the room layout but are optional: - patient/staff call (although required when for patient use); The following items may be provided: - a tip-up seat
| ADB | [7 empty] | Room Environmental Data
V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL006 |  | PULL CORD, patient/staff call (help) with reassurance lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SEA004 |  | SEAT, bench, wall mounted, 480H 1300W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0923
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V0923 |  |  |  |  | WC: independent wheelchair/semi-ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Independent wheelchair accessible toilet and adjacent hand-rinse basin may be used. 2) Call systems may be used. 3) Toilet may be used by semi-ambulant person. 4) Hand-rinse basin may be used.
| Personnel: | [6 empty] | 1 x person. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 5.5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The hand-wash basin is only suitable for ambulant and semi-ambulant users. The call repeat lamp is situated over the door outside the room. The following items are shown on the drawing but are optional: - the bin for the disposal of sanitary towels is only required in female WCs; -sanitary dispenser; - mirror, light and shaver outlet.
| ADB | [7 empty] | Room Environmental Data
V0923
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V0923 |  |  |  |  | WC: independent wheelchair/semi-ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 20
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0923
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V0923 |  |  |  |  | WC: independent wheelchair/semi-ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0923
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V0923 |  |  |  |  | WC: independent wheelchair/semi-ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAC002 |  | BACKREST, WC/toilet, padded, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BAS107 |  | BASIN, medium, general pattern, vitreous china, 2 tap holes, no overflow, bottom outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL006 |  | PULL CORD, patient/staff call (help) with reassurance lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CIS005 |  | CISTERN WC/toilet, concealed, reversible. To suit WC | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG063 |  | LUMINAIRE, single fluorescent lamp, wall, 8 watt, 300 mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR002 |  | MIRROR, wall mounted, 900H 300W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT025 |  | SOCKET outlet, shaver | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | RAI048 |  | RAIL, grab, vertical, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI159 |  | RAIL, grab, horizontal, with supports, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI161 |  | RAIL, grab, horizontal, wall or door mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI172 |  | RAIL, grab, hinged, wall mounted, 650mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP347 |  | TAP, pillar, short lever, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WCH005 |  | WC/toilet pan with seat, 700 mm projection, hospital pattern, rimless pan, vitreous china. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS015 |  | DISPENSER, toilet paper, dispense individual sheets, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE100 |  | SHELF, raised edge, non-breakable, 600W 200D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE102 |  | SHELF, raised edge, non-breakable, 200W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | VEN003 |  | VENDING MACHINE, sanitary towel with coin slot | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN028 |  | BIN, disposal, sealed, operated with one hand, nominal 420H 155W 490D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL003 |  | HOLDER, sack, small, freestanding | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Toilet may be used by ambulant person. 2) Hand-rinse basin may be used.
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following items are shown on the drawing but are optional: - the bin for the disposal of sanitary towels is only required in female WCs; - the shelf next to the basin.
| ADB | [7 empty] | Room Environmental Data
V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 20
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CIS005 |  | CISTERN WC/toilet, concealed, reversible. To suit WC | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WCH001 |  | WC/toilet pan with seat, 520-550 projection, hospital pattern, rimless pan, vitreous china. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL016 |  | HOLDER, toilet roll, multi, large | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN028 |  | BIN, disposal, sealed, operated with one hand, nominal 420H 155W 490D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL004 |  | HOLDER, sack, with lid foot operated, small, freestanding | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Shower may be used by ambulant person. 2) User may undress and dress in privacy. 3) Hanging outdoor clothing. 4) Hanging clothes and towels.
| Personnel: | [6 empty] | 1 x person (staff or visitor). Intermittent use.
| Planning Relationships: | [5 empty] | Associated with staff changing area. Close to a WC.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2.5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | This room is not recommended for patient use. The following items may be provided: - inward opening door; - full length mirror.
| ADB | [7 empty] | Room Environmental Data
V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 100-150
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | DIS200 |  | DISH, soap, wall mounted | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG063 |  | LUMINAIRE, single fluorescent lamp, wall, 8 watt, 300 mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR002 |  | MIRROR, wall mounted, 900H 300W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT025 |  | SOCKET outlet, shaver | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI260 |  | RAIL for shower curtain, 1000mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SEA024 |  | SEAT, tip-up, wall mounted, 400 W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO009 |  | SHOWER TRAY ceramic slip resistant base, with drainage outlet, 800W 800D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO018 |  | SHOWER, valve, thermostatic mixer (associated with SHO020). | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO020 |  | SHOWER, adjustable shower head hand spray (associated with SHO018). | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC014 |  | SWITCH 5amp ac single pole, 1 way, ceiling pull cord | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W1585
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | W1585 |  |  |  |  | Store: general
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Miscellaneous equipment is stored. 2) Non-clinical supplies are stored.
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2400
Notes:
| ADB | [7 empty] | Room Environmental Data
W1585
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | W1585 |  |  |  |  | Store: general
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200/300 |  | Subject to perception of detail required
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W1585
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | W1585 |  |  |  |  | Store: general
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W1585
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | W1585 |  |  |  |  | Store: general
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 20 |  |  | 20 |  |  |  |  | SHE211 |  | SHELF, 900W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SMF011 |  | SHELVING FRAME, modular storage, 1 bay, with 5 shelves, 2130H 1000W 465D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0642
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | Y0642 |  |  |  |  | Disposal hold: 1700 litres
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Holding domestic, clinical and recyclable waste for disposal or reprocessing
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Adjacent to main circulation route.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2700
Ceiling height must allow bin lids to open fully.
| Notes: | [7 empty] | Separate bins/areas must be provided for: - clinical waste; - domestic waste; - recyclable items; - linen; - equipment requiring reprocessing.
| ADB | [7 empty] | Room Environmental Data
Y0642
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | Y0642 |  |  |  |  | Disposal hold: 1700 litres
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0642
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | Y0642 |  |  |  |  | Disposal hold: 1700 litres
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley, & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0642
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | Y0642 |  |  |  |  | Disposal hold: 1700 litres
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BIN034 |  | BIN wheelie, 240 litre, 1060H 600W 730D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | BIN038 |  | BIN wheelie, 1100 litre, 1470H1370W 1115D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0642-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | Y0642-01 |  |  |  |  | Hold: disposal, dual access
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Holding domestic, clinical and recyclable waste for disposal or reprocessing
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Adjacent to main circulation route.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2700
Ceiling height must allow bin lids to open fully.
| Notes: | [7 empty] | Separate bins/areas must be provided for: - clinical waste; - domestic waste; - recyclable items; - linen; - equipment requiring reprocessing.
| ADB | [7 empty] | Room Environmental Data
Y0642-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | Y0642-01 |  |  |  |  | Hold: disposal, dual access
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
Type Of Control:
Daytime General Service Illuminance (Lux):
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | N
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0642-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | Y0642-01 |  |  |  |  | Hold: disposal, dual access
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel, trolley & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0642-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | Y0642-01 |  |  |  |  | Hold: disposal, dual access
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BIN034 |  | BIN wheelie, 240 litre, 1060H 600W 730D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | BIN038 |  | BIN wheelie, 1100 litre, 1470H1370W 1115D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0646-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | Y0646-01 |  |  |  |  | Disposal hold: 3000 litres: dual access
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Holding domestic, clinical and recyclable waste for disposal or reprocessing
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Adjacent to main circulation route.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
Ceiling height must allow bin lids to open fully.
| Notes: | [7 empty] | Separate bins/areas must be provided for: - clinical waste; - domestic waste; - recyclable items; - linen; - equipment requiring reprocessing.
| ADB | [7 empty] | Room Environmental Data
Y0646-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | Y0646-01 |  |  |  |  | Disposal hold: 3000 litres: dual access
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0646-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | Y0646-01 |  |  |  |  | Disposal hold: 3000 litres: dual access
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel, trolley & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0646-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | Y0646-01 |  |  |  |  | Disposal hold: 3000 litres: dual access
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BIN037 |  | BIN wheelie, 770 litre, 1360H1360W 800D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Disposal of liquid waste. 2) Filling and emptying cleaning equipment and containers. 3) Holding/storing cleaning equipment. 4) Cleaning equipment may be parked and/or stored. 5) Hand-rinse basin may be used. 6) Sink may be used. 7) Janitorial unit may be used.
| Personnel: | [6 empty] | 2 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Close to areas served.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
If large equipment is stored elsewhere, the size of this room can be reduced.
| Notes: | [7 empty] | This room represents a typical traditional cleaners' room with space for storing a vacuum cleaner, scrubbing/polishing machine (for hard floors) and mop and bucket (stored on the cleaners' trolley). It includes a combined bucket sink and hand-rinse basin (janitorial unit) and separate sink. The following items are shown on the room layout but are optional: - small cube lockers.
| ADB | [7 empty] | Room Environmental Data
Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 22
| Unified Glare Rating Limit (UGRL): | [13 empty] | 80
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Heat
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN20 |  |  |  |  | Mortuary and post-mortem room facilities - list of spaces
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | HOO020 |  | HOOK, single, large, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE231 |  | SHELF, 1500W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SIN013 |  | SINK and BASIN combination Janitorial unit, hinged bucket grating to sink and monobloc mixer tap with swivel nozzle, stainless steel, 900H 500W 600D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SNU012 |  | SINK UNIT, single bowl with right hand drainer, no tap holes, 1200W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLI017 |  | CLIP, spring, 32mm dia. 3, mounted on a wooden batten, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | LOC012 |  | LOCKER, wall mounted, 340H 300W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLE008 |  | SCRUBBING/POLISHING MACHINE, single brush, 110v machine | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CLE018 |  | CLEANER VACUUM, dry suction, tub, with accessories, filtered air exhaust | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | CON061 |  | CONE, warning, 'wet floor' | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL014 |  | HOLDER, sack, with lid foot operated, large, capacity 120 litre, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAD002 |  | LADDER, 3 tread, platform type 750mm height, folding | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO068 |  | TROLLEY, cleaners, mop bucket, 3 shelves tray and waste sack holder, 980H 1170W 550D | [16 empty] | 3
Activity DataBase
2016-12-29