## Sheet1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | D0434-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | D0434-01 |  |  |  |  | Rest room with beverages & snack preparation bay: 10 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Rest and relaxation or sleeping. 2) Small amounts of dry goods are stored in cupboard(s). 3) Holding/ storing food in refrigerator. 4) Crockery and cutlery are washed mechanically. 5) Hand-rinse basin may be used. 6) Consuming beverages, meals and snacks. 7) People preparing beverages, meals and snacks. 8) Telephone may be used and messages taken. 9) Laptop computer(s) may be used.
| Personnel: | [6 empty] | 10 x persons..
| Planning Relationships: | [5 empty] | Staff use - located away from public areas.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 20.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The following items are shown on the room layout but are optional: - telephone outlet; - mini kitchen water boiler; - mini kitchen microwave. The following items may be provided: - cube lockers for personal belongings; - television, radio - generally not in staff rest areas; - water cooler, or access. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
D0434-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | D0434-01 |  |  |  |  | Rest room with beverages & snack preparation bay: 10 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 – 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V/EM
| Daytime General Service Illuminance (Lux): | [13 empty] | 50 |  | Floor
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 200 |  | On tables
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 300 |  | At servery counter
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | D0434-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | D0434-01 |  |  |  |  | Rest room with beverages & snack preparation bay: 10 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | D0434-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | D0434-01 |  |  |  |  | Rest room with beverages & snack preparation bay: 10 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP715 |  | CUPBOARD, base, including sink panel, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP731 |  | CUPBOARD/DRAWER UNIT, base, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT301 |  | OUTLET, cold water for equipment | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP359 |  | TAP, pillar, high neck, long lever, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAT003 |  | WATER BOILER, 2.5 litre, electric, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WRT221 |  | WORKTOP, dished, stainless steel, with integral centre sink bowl and 2 tap holes, 2100W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP252 |  | CUPBOARD, 2 adjustable shelves, wall mounted, 750H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP259 |  | CUPBOARD, space for built in microwave, wall mounted, 750H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | OVE016 |  | OVEN, microwave, capacity 18 litre, build in, (suitable for CUP259) | [16 empty] | 2
| 8 |  |  | 8 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF058 |  | REFRIGERATOR, capacity 160 litre, automatic defrost, stainless steel, underbench, external temperature gauge, lockable, on castors, 850H 610W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB007 |  | TABLE, 710H 900W 900D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | D0434-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | D0434-03 |  |  |  |  | Rest room with beverages & snack preparation bay: 20 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Rest and relaxation or sleeping. 2) Small amounts of dry goods are stored in cupboard(s). 3) Holding/ storing food in refrigerator. 4) Crockery and cutlery are washed mechanically. 5) Hand-rinse basin may be used. 6) Consuming beverages, meals and snacks. 7) People preparing beverages, meals and snacks. 8) Telephone may be used and messages taken. 9) Laptop computer(s) may be used.
| Personnel: | [6 empty] | 20 x persons..
| Planning Relationships: | [5 empty] | Staff use - located away from public areas.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 35.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The following items are shown on the room layout but are optional: - telephone outlet; - mini kitchen water boiler; - mini kitchen microwave. The following items may be provided: - cube lockers for personal belongings; - television, radio - generally not in staff rest areas; - water cooler, or access. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
D0434-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | D0434-03 |  |  |  |  | Rest room with beverages & snack preparation bay: 20 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 – 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V/EM
| Daytime General Service Illuminance (Lux): | [13 empty] | 50 |  | Floor
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 200 |  | On tables
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 300 |  | At servery counter
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | D0434-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | D0434-03 |  |  |  |  | Rest room with beverages & snack preparation bay: 20 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | D0434-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | D0434-03 |  |  |  |  | Rest room with beverages & snack preparation bay: 20 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP715 |  | CUPBOARD, base, including sink panel, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP731 |  | CUPBOARD/DRAWER UNIT, base, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT301 |  | OUTLET, cold water for equipment | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP359 |  | TAP, pillar, high neck, long lever, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAT003 |  | WATER BOILER, 2.5 litre, electric, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WRT221 |  | WORKTOP, dished, stainless steel, with integral centre sink bowl and 2 tap holes, 2100W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP252 |  | CUPBOARD, 2 adjustable shelves, wall mounted, 750H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP259 |  | CUPBOARD, space for built in microwave, wall mounted, 750H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | OVE016 |  | OVEN, microwave, capacity 18 litre, build in, (suitable for CUP259) | [16 empty] | 2
| 16 |  |  | 16 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF058 |  | REFRIGERATOR, capacity 160 litre, automatic defrost, stainless steel, underbench, external temperature gauge, lockable, on castors, 850H 610W 600D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB135 |  | TABLE, 710H 1500W 900D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | D0434-04
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | D0434-04 |  |  |  |  | Rest room: 30 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Rest and relaxation or sleeping. 2) Laptop computer(s) may be used. 3) Telephone may be used and messages taken.
| Personnel: | [6 empty] | 30 x persons..
| Planning Relationships: | [5 empty] | Staff use - located away from public areas. Easy access to pantry
| Space Data: | [6 empty] | Area (m²): |  |  |  | 45.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The following items may be provided: - cube lockers for personal belongings; - television, radio - generally not in staff rest areas; - water cooler, or access. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
D0434-04
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | D0434-04 |  |  |  |  | Rest room: 30 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 – 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V/EM
| Daytime General Service Illuminance (Lux): | [13 empty] | 50 |  | Floor
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 200 |  | On tables
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 90
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | D0434-04
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | D0434-04 |  |  |  |  | Rest room: 30 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | D0434-04
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | D0434-04 |  |  |  |  | Rest room: 30 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 26 |  |  | 26 |  |  |  |  | CHA305 |  | CHAIR, easy, low back, upholstered, wipeable | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 7 |  |  | 7 |  |  |  |  | TAB053 |  | TABLE, occasional, square, 415H 610W 610D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB135 |  | TABLE, 710H 1500W 900D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | G0530
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | G0530 |  |  |  |  | Lobby: laboratory, high risk/containment level 3
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 15/04/2013
| Activities: | [5 empty] | 1) Holding of protective clothing for staff entering and leaving the laboratory area. 2) Clinical hand washing. 3) Using first aid (drench shower) in emergency. 4) Disposal of used protective clothing.
Personnel:
| Planning Relationships: | [5 empty] | Entrance/exit to the room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | See HBN Pathology Appendix 9 for 'Regulations and guidance relating to containment laboratories'.
| ADB | [7 empty] | Room Environmental Data
G0530
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | G0530 |  |  |  |  | Lobby: laboratory, high risk/containment level 3
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 15/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | Cascade
| Pressure Relative to Adjoining Space: | [13 empty] | +Ve
| Supply Air: Final Filter Class | [12 empty] | >H10
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Air passes from corridor through lobby into lab. Extract from lab filtered using HEPA filter to protect others. Refer to HSE regulations.
LIGHTING
Type Of Control:
Daytime General Service Illuminance (Lux):
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | N
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | G0530
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | G0530 |  |  |  |  | Lobby: laboratory, high risk/containment level 3
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 15/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | G0530
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | G0530 |  |  |  |  | Lobby: laboratory, high risk/containment level 3
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 15/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT210 |  | SOCKET outlet two-way communication system (intercom). | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT345 |  | OUTLET, floor drainage and grating, 150 mm dia. hospital pattern. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO002 |  | SHOWER, slip resistant floor with drainage outlet, 900W 900D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO025 |  | DRENCH SHOWER chain operated | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL004 |  | HOLDER, sack, with lid foot operated, small, freestanding | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | H1304-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | H1304-01 |  |  |  |  | Seminar room: 10 places (including 1 wheelchair place)
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Seminars/conferences are held. 2) Multimedia equipment may be used. 3) Laptop computer(s) may be used. 4) Telephone(s) may be used.
| Personnel: | [6 empty] | 11 x persons (including lecturer). Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 19.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | For flexibility in use, direct access to a store is required. The call repeat lamp is situated over the door outside the room. The following items may be provided: - a TV; - an overhead projector; - video-conferencing facilities; - an induction loop hearing system; - a public address system (in larger seminar rooms); - a clinical wash-hand basin and gel dispenser to allow for clinical use of the room; - audiovisual links to clinical areas for training purposes; - shelving, desks/tables and computers for training use. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
H1304-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | H1304-01 |  |  |  |  | Seminar room: 10 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 100-150 |  | On floor
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 300 |  | Over working plane
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 52
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 52 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | H1304-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | H1304-01 |  |  |  |  | Seminar room: 10 places (including 1 wheelchair place)
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control. Blinds will be required to darken room, full blackout is rarely required Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | H1304-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | H1304-01 |  |  |  |  | Seminar room: 10 places (including 1 wheelchair place)
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 12 |  |  | 12 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT004 |  | OUTLET cable, fused, 13 amp, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 10 |  |  | 10 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT135 |  | SOCKET outlet, computer data, single, ceiling mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SCR043 |  | SCREEN, projection, ceiling mounted, 1800H 1800W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC034 |  | SWITCH, dimmer, modulating | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA006 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 1200H1800W | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | PRO026 |  | PROJECTOR, multi-media, ceiling mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA051 |  | BOARD, flip chart, height adjustable, freestanding | [16 empty] | 3
| 10 |  |  | 10 |  |  |  |  | CHA318 |  | CHAIR, upright, with arms, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP036 |  | CUPBOARD, steel, 2 adjustable shelves, 2 door, lockable, 900H 900W 420D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB008 |  | TABLE, 710H 1200W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0114
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0114 |  |  |  |  | Store and preparation area: chemicals No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Storing a working supply of: a) reagents and solutions. b) flammable and toxic chemicals. 2) Provision of refrigerated storage. 3) Weighing and preparation of chemicals and reagents for use in general and special tests laboratory areas. 4) Holding of glassware and other equipment for use in the preparation of reagents. 5) Displaying notices. 6) Holding of protective clothing for staff entering and leaving the laboratory area. 7) Disposal of used protective clothing. 8) Clinical hand washing.
| Personnel: | [6 empty] | Up to 2 staff
| Planning Relationships: | [5 empty] | Easy access to laboratory.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 10.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | A glass wash facility should be associated with the chemical storage and preparation area.
| ADB | [7 empty] | Room Environmental Data
L0114
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0114 |  |  |  |  | Store and preparation area: chemicals No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 20
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | n/a
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 84
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 84 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | ionisation detector to be considered if accelerants present
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0114
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0114 |  |  |  |  | Store and preparation area: chemicals No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0114
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0114 |  |  |  |  | Store and preparation area: chemicals No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWB075 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 1500W 750D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWS175 |  | WORKTOP, with sink on right (sink size 200x450x365), 920H 1500W 750D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 10 |  |  | 10 |  |  |  |  | SHE590 |  | SHELF, 1000W300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB046 |  | CABINET, poisons, wall mounted, 600H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB031 |  | OVEN, hot air, low temperature, 920H 962W 898D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB033 |  | BENCH MAGNIFIER, with fluorescent lamp, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | BAL003 |  | BALANCE, top plan, capacity 4500g, increments 0.01g, 130H 185W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | BAL008 |  | BALANCE, analytical, 510g, 415H 240W 520D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP560 |  | CUPBOARD, metal, epoxy resin lined, flame resistant, lockable, 815H 760W 470D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB037 |  | HOT PLATE, 85H 225W 340D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB051 |  | STIRRER, magnetic, 85H 225W 340D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB067 |  | JAR, desiccator, with sealing ring, guaze and PTFE stopcock, 432H 375 dia. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MET005 |  | METER, pH., 190H 170L 260D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0114
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0114 |  |  |  |  | Store and preparation area: chemicals No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | REF066 |  | REFRIGERATOR, capacity 390 litres, 1855H 645W 595D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0115
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0115 |  |  |  |  | Store and preparation area: chemicals No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Storing a working supply of: a) reagents and solutions. b) flammable and toxic chemicals. 2) Provision of refrigerated storage. 3) Weighing and preparation of chemicals and reagents for use in general and special tests laboratory areas. 4) Holding of glassware and other equipment for use in the preparation of reagents. 5) Displaying notices. 6) Holding of protective clothing for staff entering and leaving the laboratory area. 7) Disposal of used protective clothing. 8) Clinical hand washing.
| Personnel: | [6 empty] | Up to 3 staff
| Planning Relationships: | [5 empty] | Easy access to laboratory.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | A glass wash facility should be associated with the chemical storage and preparation area.
| ADB | [7 empty] | Room Environmental Data
L0115
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0115 |  |  |  |  | Store and preparation area: chemicals No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 20
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | n/a
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 85
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 85 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | ionisation detector to be considered if accelerants present
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0115
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0115 |  |  |  |  | Store and preparation area: chemicals No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0115
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0115 |  |  |  |  | Store and preparation area: chemicals No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | LWB075 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 1500W 750D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWS175 |  | WORKTOP, with sink on right (sink size 200x450x365), 920H 1500W 750D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 10 |  |  | 10 |  |  |  |  | SHE590 |  | SHELF, 1000W300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB046 |  | CABINET, poisons, wall mounted, 600H 600W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB031 |  | OVEN, hot air, low temperature, 920H 962W 898D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB033 |  | BENCH MAGNIFIER, with fluorescent lamp, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | BAL003 |  | BALANCE, top plan, capacity 4500g, increments 0.01g, 130H 185W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | BAL008 |  | BALANCE, analytical, 510g, 415H 240W 520D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP560 |  | CUPBOARD, metal, epoxy resin lined, flame resistant, lockable, 815H 760W 470D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB037 |  | HOT PLATE, 85H 225W 340D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB051 |  | STIRRER, magnetic, 85H 225W 340D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB067 |  | JAR, desiccator, with sealing ring, guaze and PTFE stopcock, 432H 375 dia. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MET005 |  | METER, pH., 190H 170L 260D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0115
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0115 |  |  |  |  | Store and preparation area: chemicals No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | REF066 |  | REFRIGERATOR, capacity 390 litres, 1855H 645W 595D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0118
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0118 |  |  |  |  | Laboratory: Chemical pathology, urgent test No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from chemical pathology reception or preparation area. 2) Carrying out preparation prior to testing specimens. 3) Testing of specimens by special procedures for steroids and drugs. 4) Testing of specimens by special procedures for toxicology. 5) Testing of specimens by special procedures for protein. 6) Testing of specimens by special procedures for chromatography. 7) Testing of specimens by special procedures for immuno-assay. 8) Testing of specimens by special procedures for trace metals. 9) Testing of specimens by special procedures for glycosylated haemoglobin. 10) Reading and recording results and writing reports. 11) Holding of "in use" reagents, solutions in small and large volumes disposables and small items of laboratory equipment. 12) Storage of samples/specimens under refrigerated/deep freeze conditions. 13) Displaying notices. 14) Holding of protective clothing for staff entering and leaving the laboratory area. 15) Clinical hand washing.
| Personnel: | [6 empty] | Up to 3 staff
| Planning Relationships: | [5 empty] | Easy access to General Laboratory. Easy access from Specimen Reception/Preparation & Preliminary Processing area/despatch area. Easy access to Chemical Store/Weighing/Reagent-solution Prep. area. Easy access to Cold room. Convenient access from Consultant's, Junior Medical staff, Grade 3/4 technician's, secretarial offices & departmental records.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Refrigerated storage to include reagents. Consideration of pipe runs from manifold for gases is required. Deionised water should be provided using resin based filter or points of use.
| ADB | [7 empty] | Room Environmental Data
L0118
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0118 |  |  |  |  | Laboratory: Chemical pathology, urgent test No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 86
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 86 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0118
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0118 |  |  |  |  | Laboratory: Chemical pathology, urgent test No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0118
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0118 |  |  |  |  | Laboratory: Chemical pathology, urgent test No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP145 |  | CUPBOARD, fume, separate extract and removable worktop floor standing, 2400H 1500W 900D | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | DRA008 |  | DRAINAGE, catchpot | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DRI021 |  | DRIP CUP, deck mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO008 |  | HOOD, extract, 1800W 700D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | LWB055 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1500W 750D, HTM67 | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | LWB090 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 3000W 750D, HTM67 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWS175 |  | WORKTOP, with sink on right (sink size 200x450x365), 920H 1500W 750D, HTM67 | [16 empty] | 1
| 21 |  |  | 21 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 15 |  |  | 15 |  |  |  |  | SHE590 |  | SHELF, 1000W300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SIN076 |  | SINK, inset, ceramic, 250H 500W 400D | [16 empty] | 1
| 20 |  |  | 20 |  |  |  |  | SPI010 |  | SPINE UNIT, laboratory, 1000 length | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | TAP022 |  | TAP, laboratory, cold water | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP035 |  | TAP laboratory remote control extension spindle | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP060 |  | TAP laboratory water demineralised | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP399 |  | TAP laboratory acetylene | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP415 |  | TAP laboratory hydrogen | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP419 |  | TAP laboratory nitrogen | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP426 |  | TAP laboratory oxygen | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP429 |  | TAP laboratory argon | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP430 |  | TAP laboratory gas | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CEN016 |  | CENTRIFUGE, refrigerated, floor standing, 1140H 760W 990D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLO001 |  | CLOCK battery, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB040 |  | GAS CHROMATOGRAPHY equipment, 463H 250W 363D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | REF103 |  | REFRIGERATED DEEP FREEZE, capacity 327 litres, vertical type, sparkfree interior, 1840H 660W 685D | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0118
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0118 |  |  |  |  | Laboratory: Chemical pathology, urgent test No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | CEN012 |  | CENTRIFUGE, floor standing, mobile, 700H 670W 720D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 7 |  |  | 7 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP560 |  | CUPBOARD, metal, epoxy resin lined, flame resistant, lockable, 815H 760W 470D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB038 |  | H.P.L.C. EQUIPMENT (high pressure liquid chromatography) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB041 |  | DETECTOR, (to be used with Gas Chromatography equipment), 90H 270W 350D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB042 |  | FLUOROMETER, 175H 390W 310D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB044 |  | ELECTROPHORESIS EQUIPMENT, power pack 120H 300W 280D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB045 |  | ELECTROPHORESIS EQUIPMENT, bath | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB046 |  | E.L.I.S.A. EQUIPMENT, dispenser (Enzyme linked immuno sorbent assay) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB047 |  | E.L.I.S.A. EQUIPMENT, washer (Enzyme linked immuno sorbent assay) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB048 |  | E.L.I.S.A. EQUIPMENT, plate reader (Enzyme linked immuno sorbent assay) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB049 |  | THIN LAYER CHROMATOGRAPHY, equipment | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB050 |  | SCANNER, thin layer chromatography (TLC), 345H 620W 620D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB051 |  | STIRRER, magnetic, 85H 225W 340D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB052 |  | MIXER, vortex | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB092 |  | BATH, water, electrothermal, boiling, with flat lid and rings | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SPE006 |  | SPECTROPHOTOMETER, Double beam UV/VIS | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SPE007 |  | SPECTROPHOTOMETER, ultra violet and recording, Microprocessor controlled single beam with touch screen, stores 50 methods and sets of date | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SPE008 |  | SPECTROPHOTOMETER, atomic absorption and printer | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0201
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0201 |  |  |  |  | Automated laboratory No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Automated processes for routine or emergency tests of chemical pathology and haemotology. 2) Reading and recording results and writing reports. 3) Holding of "in use" reagents, solutions in small and large volumes disposables and small items of laboratory equipment. 4) Storage of samples/specimens under refrigerated/deep freeze conditions. 5) Displaying notices. 6) Holding of protective clothing for staff entering and leaving the laboratory area.
| Personnel: | [6 empty] | Up to 4 staff
| Planning Relationships: | [5 empty] | Easy access from specimen sorting and request processing area. Easy access to senior staff office.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 189 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | For full details see HBN Pathology Para 4.63
| ADB | [7 empty] | Room Environmental Data
L0201
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0201 |  |  |  |  | Automated laboratory No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 87
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 87 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0201
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0201 |  |  |  |  | Automated laboratory No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0201
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0201 |  |  |  |  | Automated laboratory No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 10 |  |  | 10 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT081 |  | CONNECTION BOX 32amp single phase | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT086 |  | CONNECTION BOX 63amp single phase | [16 empty] | 1
| 14 |  |  | 14 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | UPS006 |  | UPS 6KVA for 2 x biochem analysis system | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | UPS007 |  | UPS 6KVA for 2 x immunochem analysis | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | UPS010 |  | UPS 10KVA for pre-analysis system | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO001 |  | CLOCK battery, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP149 |  | CUPBOARD, fume, bench mounted, 1145H 1200W 570D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | WAS051 |  | WASH, eye, first aid, with mirror, wall mounted, 360H 250W 100D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | ANA057 |  | ANALYSER, blood gas, 490H 410W 460D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CEN011 |  | CENTRIFUGE, refrigerated, bench mounted, 395H 640W 595D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | COM024 |  | AUTO PC WORKSTATION, 450H 750W 500D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB078 |  | MACHINE, slide drying, linear, 155H 1050W 155D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB151 |  | AUTO INPUT BUFFER, capacity: up to 300 samples (in 2 trays), 900H 1200W 800D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB152 |  | AUTO CENTRIFUGE MODULE, throughput: upto 250 s/hr (at 5 minutes spin time), 900H 800W 800D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB153 |  | AUTO DESTOPPER MODULE, throughput: up to 400 s/hr, 900H 600W 800D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB154 |  | AUTO ON-LINE ALIQUOTTER MODULE, 900H 1500W 800D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB155 |  | AUTO OFF-LINE ALIQUOTTER MODULE, 1500H 1200W 800D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB156 |  | AUTO BAR CODE LABELER MODULE, throughput: up to 450 s/hr, 1350H 450W 800D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB157 |  | AUTO RESTOPPER MODULE, throughput: up to 500 s/hr, 1400H 450W 800D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB158 |  | AUTO ALIQUOT SAMPLE SORTER MODULE, 1400H 750W 800D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB159 |  | AUTO OUTPUT BUFFER MODULE, capacity: up to 300 (in 2 trays), 900H 750W 800D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB161 |  | MODULAR PRE-ANALYTICAL system | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB162 |  | AUTO STAT PORT, 900H 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB163 |  | AUTO ANALYSER biochemistry, 900H 1200W 800D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB165 |  | AUTO ANALYSER immunochemistry, 900H 1200W 800D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0201
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0201 |  |  |  |  | Automated laboratory No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | LAB166 |  | AUTO CORE TRACK sys length to suit chemo/immuno, 900H 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB170 |  | ANALYSER ESR AUTO, 300H 450W 350D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB171 |  | ANALYSER COAGULATION AUTO, 400H 1020W 720D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB175 |  | SLIDE MAKING SYSTEM HAEMATOLOGY AUTOMATED, 540H 540W 240D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB176 |  | AUTO CORE TRACK SYS TO SUIT ( HAEMATOLOGY), 900H 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB177 |  | AUTO INPUT LOADER HAEMATOLOGY | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB178 |  | AUTO CORE TRACK sys to suit (Haematology) | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB179 |  | ANALYSER HAEMATOLOGY HIGH THROUHGPUT, 720H 720W 920D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF042 |  | REFRIGERATED DEEP FREEZE CABINET, capacity 243 litres, internal temperature gauge, 1450H 600W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF067 |  | REFRIGERATOR, capacity 385 litre, automatic defrost, stainless steel, external temperature gauge, lockable, on castors, 1995H 600W 700D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0204
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0204 |  |  |  |  | Automated laboratory Version 2, with emergency shower No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Automated processes for routine or emergency tests of chemical pathology and haemotology. 2) Reading and recording results and writing reports. 3) Holding of "in use" reagents, solutions in small and large volumes disposables and small items of laboratory equipment. 4) Storage of samples/specimens under refrigerated/deep freeze conditions. 5) Displaying notices. 6) Holding of protective clothing for staff entering and leaving the laboratory area. 7) Clinical hand washing. 8) Using first aid (drench shower) in emergency.
| Personnel: | [6 empty] | Up to 6 staff
| Planning Relationships: | [5 empty] | Easy access from specimen sorting and request processing area. Easy access to senior staff office.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 252 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | For full details see HBN Pathology Para 4.63 Central link Data manager (LAN with no PC'S as required).
| ADB | [7 empty] | Room Environmental Data
L0204
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0204 |  |  |  |  | Automated laboratory Version 2, with emergency shower No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 88
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 88 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0204
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0204 |  |  |  |  | Automated laboratory Version 2, with emergency shower No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0204
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0204 |  |  |  |  | Automated laboratory Version 2, with emergency shower No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 10 |  |  | 10 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 14 |  |  | 14 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT345 |  | OUTLET, floor drainage and grating, 150 mm dia. hospital pattern. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | REF032 |  | FREEZER upright -20 deg.C, 2000H 800W 1000D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO002 |  | SHOWER, slip resistant floor with drainage outlet, 900W 900D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO025 |  | DRENCH SHOWER chain operated | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | WOR031 |  | WORKBENCH laboratory stainless steel, with sink | [16 empty] | 1
| 10 |  |  | 10 |  |  |  |  | WOR037 |  | WORKBENCH laboratory stainless steel, downdraught, left hand plain top, with sink and disposal unit, 850H 1200W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAB007 |  | CABINET utility, 100H 100W 500D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP149 |  | CUPBOARD, fume, bench mounted, 1145H 1200W 570D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | WAS051 |  | WASH, eye, first aid, with mirror, wall mounted, 360H 250W 100D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | ANA057 |  | ANALYSER, blood gas, 490H 410W 460D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CEN011 |  | CENTRIFUGE, refrigerated, bench mounted, 395H 640W 595D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM026 |  | PC LINE MASTER | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB167 |  | ANALYSER CHEMISTRY AUTO 2400 TESTS/H, 1130H 1480W 860D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB168 |  | ANALYSER CHEMISTRY AUTO 1650 TESTS/H, 1160H 171W 940D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0204
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0204 |  |  |  |  | Automated laboratory Version 2, with emergency shower No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | LAB169 |  | ANALYSER IMMUNOASSAY AUTO 240 TESTS/, 1040H 1840W 105D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB173 |  | ANALYSER HAEMATOLOGY 120 TESTS/HR, 860H 1410W 680D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB181 |  | SAMPLE DISTRIBUTION SYSTEM | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB184 |  | SAMPLE MANAGER LOAD/UNLOAD, 100H 100W 400D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF066 |  | REFRIGERATOR, capacity 390 litres, 1855H 645W 595D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0301
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0301 |  |  |  |  | Laboratory: Microbiology No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from specimen reception. 2) Sorting, batching and labelling/numbering specimens and processing request forms. 3) Transferring batched specimens to main laboratory/bench/automated machine with request forms. 4) Carrying out general bacteriological investigations, culture identification and sensitivity testing. 5) Centrifugation of samples/specimens (urine, blood, fluids). 6) Staining of slide preparations. 7) Carrying out examination of specimens using a microscope. 8) Preparing inoculated media for anaerobic investigation inc. evacuation of air from anaerobic jars and incubation under anaerobic conditions. 9) Incubation of culture media in special conditions (e.g. C02) and temperatures. 10) Notes and/or reports may be written. 11) Holding laboratory manuals, reference books. 12) Holding of "in use" reagents, flammable solvents, laboratory media and small items of equipment. 13) Storage of samples/specimens under refrigerated/deep freeze conditions. 14) Disposal of liquid waste. 15) Displaying notices. 16) Holding of protective clothing for staff entering and leaving the laboratory area. 17) Clinical hand washing.
| Personnel: | [6 empty] | 1 - 2 staff per workstation.
| Planning Relationships: | [5 empty] | Easy access from laboratory main specimen reception. Access to a hot room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 126 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Bacteriological investigations, culture identification & sensitivity testing mainly on the following: Urines, wound swabs, genito-urinary specimens & faeces (general microbiology) & on miscellaneous specimens e.g. cerebrospinal fluids & other fluids etc. includes: (a) plating & inoculation of appropriate culture media for isolation & identification of micro-organisms & antibiotic sensitivity testing, (b) making slides, examination of cultures, identification tests, sensitivity tests & recording results. Consideration of pipe runs from manifold for gases is required.
| ADB | [7 empty] | Room Environmental Data
L0301
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0301 |  |  |  |  | Laboratory: Microbiology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 89
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 89 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0301
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0301 |  |  |  |  | Laboratory: Microbiology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0301
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0301 |  |  |  |  | Laboratory: Microbiology No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CUP444 |  | CUPBOARD, glass sliding doors, wall mounted, 600H 1000W 300D | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | DRA008 |  | DRAINAGE, catchpot | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | LWB055 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1500W 750D, HTM67 | [16 empty] | 1
| 10 |  |  | 10 |  |  |  |  | LWB090 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 3000W 750D, HTM67 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWS175 |  | WORKTOP, with sink on right (sink size 200x450x365), 920H 1500W 750D, HTM67 | [16 empty] | 1
| 40 |  |  | 40 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 9 |  |  | 9 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 65 |  |  | 65 |  |  |  |  | SHE590 |  | SHELF, 1000W300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SIN076 |  | SINK, inset, ceramic, 250H 500W 400D | [16 empty] | 1
| 41 |  |  | 41 |  |  |  |  | SPI010 |  | SPINE UNIT, laboratory, 1000 length | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP022 |  | TAP, laboratory, cold water | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP060 |  | TAP laboratory water demineralised | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP401 |  | TAP laboratory carbon dioxide | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP415 |  | TAP laboratory hydrogen | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP419 |  | TAP laboratory nitrogen | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP426 |  | TAP laboratory oxygen | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP429 |  | TAP laboratory argon | [16 empty] | 1
| 10 |  |  | 10 |  |  |  |  | TAP430 |  | TAP laboratory gas | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB007 |  | FREEZER, -70 deg.C, floor standing, 1650H 1025W 1210D | [16 empty] | 2
| 4 |  |  | 4 |  |  |  |  | LAB033 |  | BENCH MAGNIFIER, with fluorescent lamp, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB035 |  | INCUBATOR, carbon dioxide, bench mounted, 970H 630W 680D | [16 empty] | 2
| 3 |  |  | 3 |  |  |  |  | LAB036 |  | INCUBATOR, variable temperature, 955H 640W 655D | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0301
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0301 |  |  |  |  | Laboratory: Microbiology No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | LAB040 |  | GAS CHROMATOGRAPHY equipment, 463H 250W 363D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB119 |  | INCUBATOR, anaerobic chamber, 667H 1283W 700D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF103 |  | REFRIGERATED DEEP FREEZE, capacity 327 litres, vertical type, sparkfree interior, 1840H 660W 685D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB042 |  | CABINET + cabinet dolly cart , bottle store, flammable liquids, mobile, 1040H 710W 485D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CEN017 |  | CENTRIFUGE, sealed buckets, mass 55kg, bench mounted, 340H 470W 550D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 9 |  |  | 9 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 14 |  |  | 14 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 5 |  |  | 5 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| 7 |  |  | 7 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | LAB021 |  | CABINET, slide dryer, 195H 437W 245D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | LAB024 |  | ROTARY PLATER, 100H 150W 155D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB034 |  | INOCULATOR, multi-point, 255H 410W 180D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB041 |  | DETECTOR, (to be used with Gas Chromatography equipment), 90H 270W 350D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB086 |  | COUNTER, colony, 90H 295W 325D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB117 |  | BATH, water, electrothermal, 300H 325W 720D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC020 |  | MICROSCOPE, inverted, 300H 200W 250D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | MIC025 |  | MICROSCOPE, binocular, 300H 200W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF066 |  | REFRIGERATOR, capacity 390 litres, 1855H 645W 595D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0304
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0304 |  |  |  |  | Laboratory: Microbiology, urgent tests No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from specimen reception. 2) Sorting, batching and labelling/numbering specimens and processing request forms. 3) Transferring batched specimens to main laboratory/bench/automated machine with request forms. 4) Carrying out general bacteriological investigations, culture identification and sensitivity testing. 5) Centrifugation of samples/specimens (urine, blood, fluids). 6) Staining of slide preparations. 7) Carrying out examination of specimens using a microscope. 8) Preparing inoculated media for anaerobic investigation inc. evacuation of air from anaerobic jars and incubation under anaerobic conditions. 9) Incubation of culture media in special conditions (e.g. C02) and temperatures. 10) Notes and/or reports may be written. 11) Holding laboratory manuals, reference books. 12) Holding of "in use" reagents, flammable solvents, laboratory media and small items of equipment. 13) Storage of samples/specimens under refrigerated/deep freeze conditions. 14) Disposal of liquid waste. 15) Displaying notices. 16) Holding of protective clothing for staff entering and leaving the laboratory area. 17) Clinical hand washing.
| Personnel: | [6 empty] | 1 - 3 staff
| Planning Relationships: | [5 empty] | Easy access for rapid & convenient transfer of specimens from laboratory main specimen reception. Easy access to Containment Level III room & Autoclave/wash-up area. Close to Blood culture room, Bacterial & Viral Serology & Antibiotic section & the Media preparation/plate pouring areas. Near to Hot room. Convenient access from Consultant's Junior Medical staff, Head MLSO technician's, secretarial offices & departmental records.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Bacteriological investigations, culture identification & sensitivity testing mainly on the following: Urines, wound swabs, genito-urinary specimens & faeces (general microbiology) & on miscellaneous specimens e.g. cerebrospinal fluids & other fluids etc. includes: (a) plating & inoculation of appropriate culture media for isolation & identification of micro-organisms & antibiotic sensitivity testing, (b) making slides, examination of cultures, identification tests, sensitivity tests & recording results. Consideration of pipe runs from manifold for gases is required.
| ADB | [7 empty] | Room Environmental Data
L0304
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0304 |  |  |  |  | Laboratory: Microbiology, urgent tests No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 90
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 90 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0304
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0304 |  |  |  |  | Laboratory: Microbiology, urgent tests No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0304
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0304 |  |  |  |  | Laboratory: Microbiology, urgent tests No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CUP444 |  | CUPBOARD, glass sliding doors, wall mounted, 600H 1000W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWB052 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1200W 750D, HTM67 | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | LWB055 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1500W 750D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWS175 |  | WORKTOP, with sink on right (sink size 200x450x365), 920H 1500W 750D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 7 |  |  | 7 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 15 |  |  | 15 |  |  |  |  | SHE590 |  | SHELF, 1000W300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP060 |  | TAP laboratory water demineralised | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP401 |  | TAP laboratory carbon dioxide | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP415 |  | TAP laboratory hydrogen | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP419 |  | TAP laboratory nitrogen | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP426 |  | TAP laboratory oxygen | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP429 |  | TAP laboratory argon | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP430 |  | TAP laboratory gas | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB007 |  | FREEZER, -70 deg.C, floor standing, 1650H 1025W 1210D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | LAB033 |  | BENCH MAGNIFIER, with fluorescent lamp, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB035 |  | INCUBATOR, carbon dioxide, bench mounted, 970H 630W 680D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB036 |  | INCUBATOR, variable temperature, 955H 640W 655D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB040 |  | GAS CHROMATOGRAPHY equipment, 463H 250W 363D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB119 |  | INCUBATOR, anaerobic chamber, 667H 1283W 700D | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0304
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0304 |  |  |  |  | Laboratory: Microbiology, urgent tests No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | REF103 |  | REFRIGERATED DEEP FREEZE, capacity 327 litres, vertical type, sparkfree interior, 1840H 660W 685D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB042 |  | CABINET + cabinet dolly cart , bottle store, flammable liquids, mobile, 1040H 710W 485D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CEN017 |  | CENTRIFUGE, sealed buckets, mass 55kg, bench mounted, 340H 470W 550D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB021 |  | CABINET, slide dryer, 195H 437W 245D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB024 |  | ROTARY PLATER, 100H 150W 155D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB034 |  | INOCULATOR, multi-point, 255H 410W 180D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB041 |  | DETECTOR, (to be used with Gas Chromatography equipment), 90H 270W 350D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB086 |  | COUNTER, colony, 90H 295W 325D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB117 |  | BATH, water, electrothermal, 300H 325W 720D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC020 |  | MICROSCOPE, inverted, 300H 200W 250D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC025 |  | MICROSCOPE, binocular, 300H 200W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF066 |  | REFRIGERATOR, capacity 390 litres, 1855H 645W 595D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0320
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0320 |  |  |  |  | Media preparation laboratory No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Preparation of media. 2) Filling sterilized containers or test tubes with prepared media, capping containers and placing in baskets prior to sterilization. 3) Holding of reagents, raw materials, glassware and other items. 4) Disposal of liquid waste. 5) Displaying notices. 6) Holding of protective clothing for staff entering and leaving the laboratory area. 7) Clinical hand washing.
| Personnel: | [6 empty] | Up to 2 staff
| Planning Relationships: | [5 empty] | Direct access to Media/plate pouring area. Direct access to Autoclave/wash-up area. Near to Microbiology main laboratory, Containment Level 3 Room, Bacterial & Viral diagnostic serology & antibiotic section & Blood culture room. Easy access to Main store & Microbiology store.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 10.5 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
L0320
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0320 |  |  |  |  | Media preparation laboratory No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG<BR>To plate pouring.POS to washup
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 92
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 92 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0320
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0320 |  |  |  |  | Media preparation laboratory No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0320
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0320 |  |  |  |  | Media preparation laboratory No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | LWB072 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 1200W 750D, HTM67 | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | SPI010 |  | SPINE UNIT, laboratory, 1000 length | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP430 |  | TAP laboratory gas | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB032 |  | CABINET, drying laboratory equipment, wall mounted, 530H 760W 360D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB031 |  | OVEN, hot air, low temperature, 920H 962W 898D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BAL003 |  | BALANCE, top plan, capacity 4500g, increments 0.01g, 130H 185W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | BAL008 |  | BALANCE, analytical, 510g, 415H 240W 520D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL008 |  | HOLDER, sack with lid foot operated, large, freestanding, 960H 500W 415D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB051 |  | STIRRER, magnetic, 85H 225W 340D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB082 |  | LIQUID VOLUME DISPENSER, mechanical, 300H 160W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB117 |  | BATH, water, electrothermal, 300H 325W 720D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MET005 |  | METER, pH., 190H 170L 260D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0320
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0320 |  |  |  |  | Media preparation laboratory No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | RAC425 |  | RACK, metal, 2 bays, 4 shelves, 1980H 1800W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF066 |  | REFRIGERATOR, capacity 390 litres, 1855H 645W 595D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0322
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0322 |  |  |  |  | Plate pouring and media dispensing laboratory No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Plate pouring using mechanical equipment or manually under laminar flow cabinet. 2) Dispensing prepared media into petri dishes, tubes, bottles, using mechanical equipment or manually under laminar flow cabinet. 3) Holding plates, bottles and tubes prior to use. 4) Holding refrigerated storage of culture media plates and bottles. 5) Disposal of liquid waste. 6) Displaying notices. 7) Clinical hand washing. 8) Using first aid (drench shower) in emergency.
| Personnel: | [6 empty] | Up to 2 staff
| Planning Relationships: | [5 empty] | Direct access to Media preparation area. Near to Microbiology main laboratory, Containment Level 3 Room, Bacterial & Viral diagnostic serology & antibiotic section & Blood culture room. Easy access to Main store & Microbiology store.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 10.5 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
L0322
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0322 |  |  |  |  | Plate pouring and media dispensing laboratory No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | POS<BR>To Media Preparation.
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 93
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 93 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0322
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0322 |  |  |  |  | Plate pouring and media dispensing laboratory No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0322
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0322 |  |  |  |  | Plate pouring and media dispensing laboratory No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DRA008 |  | DRAINAGE, catchpot | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWB052 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1200W 750D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWS055 |  | WORKTOP, with sink on right (sink size 200x450x365), 720H 1500W 750D, HTM67 | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT345 |  | OUTLET, floor drainage and grating, 150 mm dia. hospital pattern. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO002 |  | SHOWER, slip resistant floor with drainage outlet, 900W 900D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO025 |  | DRENCH SHOWER chain operated | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SPI010 |  | SPINE UNIT, laboratory, 1000 length | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP060 |  | TAP laboratory water demineralised | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP343 |  | *TAP pillar 12mm, high neck. HTM64TP3. Replaced by: TAP359, 15/05/06 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP430 |  | TAP laboratory gas | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB124 |  | CABINET, laminar flow, free standing, 1600H 1260W 930D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB036 |  | INCUBATOR, variable temperature, 955H 640W 655D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL008 |  | HOLDER, sack with lid foot operated, large, freestanding, 960H 500W 415D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB081 |  | MEDIA PREPARATION/POURING EQUIPMENT, mechanical | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB117 |  | BATH, water, electrothermal, 300H 325W 720D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0322
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0322 |  |  |  |  | Plate pouring and media dispensing laboratory No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0324
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0324 |  |  |  |  | Plate pouring and media dispensing laboratory No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Plate pouring using mechanical equipment or manually under laminar flow cabinet. 2) Dispensing prepared media into petri dishes, tubes, bottles, using mechanical equipment or manually under laminar flow cabinet. 3) Holding plates, bottles and tubes prior to use. 4) Holding refrigerated storage of culture media plates and bottles. 5) Disposal of liquid waste. 6) Displaying notices. 7) Clinical hand washing.
| Personnel: | [6 empty] | Up to 2 staff
| Planning Relationships: | [5 empty] | Direct access to Media preparation area. Near to Microbiology main laboratory, Containment Level 3 Room, Bacterial & Viral diagnostic serology & antibiotic section & Blood culture room. Easy access to Main store & Microbiology store.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
L0324
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0324 |  |  |  |  | Plate pouring and media dispensing laboratory No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | POS<BR>To Media Preparation.
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 94
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 94 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0324
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0324 |  |  |  |  | Plate pouring and media dispensing laboratory No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0324
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0324 |  |  |  |  | Plate pouring and media dispensing laboratory No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DRA008 |  | DRAINAGE, catchpot | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | LWB052 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1200W 750D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWS055 |  | WORKTOP, with sink on right (sink size 200x450x365), 720H 1500W 750D, HTM67 | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SPI010 |  | SPINE UNIT, laboratory, 1000 length | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP060 |  | TAP laboratory water demineralised | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP343 |  | *TAP pillar 12mm, high neck. HTM64TP3. Replaced by: TAP359, 15/05/06 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP430 |  | TAP laboratory gas | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CAB124 |  | CABINET, laminar flow, free standing, 1600H 1260W 930D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB036 |  | INCUBATOR, variable temperature, 955H 640W 655D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL008 |  | HOLDER, sack with lid foot operated, large, freestanding, 960H 500W 415D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB081 |  | MEDIA PREPARATION/POURING EQUIPMENT, mechanical | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB117 |  | BATH, water, electrothermal, 300H 325W 720D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0413
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0413 |  |  |  |  | Laboratory: Haematology, urgent tests No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from Haemotology specimen reception bench at the appropriate working area. 2) Automated or manual processing of specimens prior to or during testing of coagulation studies. 3) Automated or manual processing of specimens prior to or during testing of haemoglobinopathy-electrophoresis. 4) Automated or manual processing of specimens prior to or during testing of acute phase protein studies and red cell enzymes. 5) Reading and recording results and writing reports. 6) Holding of "in use" reagents, solutions in small and large volumes disposables and small items of laboratory equipment. 7) Storage of samples/specimens under refrigerated/deep freeze conditions. 8) Displaying notices. 9) Holding of protective clothing for staff entering and leaving the laboratory area. 10) Clinical hand washing.
| Personnel: | [6 empty] | Up to 3 staff
| Planning Relationships: | [5 empty] | Easy access for rapid & convenient transfer of specimens from Haematology specimen reception bench. Easy access to Haematology general laboratory. Convenient access from Consultant's, Junior Medical staff, Head MLSO's, secretarial offices & departmental records.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Deionised water should be provided using resin based filter or points of use.
| ADB | [7 empty] | Room Environmental Data
L0413
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0413 |  |  |  |  | Laboratory: Haematology, urgent tests No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 95
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 95 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0413
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0413 |  |  |  |  | Laboratory: Haematology, urgent tests No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0413
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0413 |  |  |  |  | Laboratory: Haematology, urgent tests No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | DRA008 |  | DRAINAGE, catchpot | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | LWB055 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1500W 750D, HTM67 | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | LWB075 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 1500W 750D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWS055 |  | WORKTOP, with sink on right (sink size 200x450x365), 720H 1500W 750D, HTM67 | [16 empty] | 1
| 16 |  |  | 16 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 16 |  |  | 16 |  |  |  |  | SHE590 |  | SHELF, 1000W300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SIN076 |  | SINK, inset, ceramic, 250H 500W 400D | [16 empty] | 1
| 15 |  |  | 15 |  |  |  |  | SPI010 |  | SPINE UNIT, laboratory, 1000 length | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP022 |  | TAP, laboratory, cold water | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP430 |  | TAP laboratory gas | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB032 |  | CABINET, drying laboratory equipment, wall mounted, 530H 760W 360D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB007 |  | FREEZER, -70 deg.C, floor standing, 1650H 1025W 1210D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB033 |  | BENCH MAGNIFIER, with fluorescent lamp, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF103 |  | REFRIGERATED DEEP FREEZE, capacity 327 litres, vertical type, sparkfree interior, 1840H 660W 685D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CEN003 |  | CENTRIFUGE bench mounted, 300H 420W 490D | [16 empty] | 3
| 5 |  |  | 5 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0413
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0413 |  |  |  |  | Laboratory: Haematology, urgent tests No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 4 |  |  | 4 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB043 |  | FIBRINOMETER, 250H 270W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB044 |  | ELECTROPHORESIS EQUIPMENT, power pack 120H 300W 280D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB045 |  | ELECTROPHORESIS EQUIPMENT, bath | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB051 |  | STIRRER, magnetic, 85H 225W 340D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB052 |  | MIXER, vortex | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB055 |  | MIXER, roller type, 5 rollers, 90H 500W 200D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB080 |  | NEPHELOMETER, 175H 250W 300D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB087 |  | COAGULATOR, mechanical, 590H 1040W 630D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB103 |  | VIEWING MIRROR, agglutination, 250H 300W 200D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB117 |  | BATH, water, electrothermal, 300H 325W 720D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF060 |  | REFRIGERATOR, reagents, capacity 110 litre, external temperature gauge, automatic defrost, underbench, 850H 500W 590D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SPE004 |  | SPECTROPHOTOMETER, ultra violet/visual wavelengths, single beam | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0506
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0506 |  |  |  |  | Specimen hold: out-of-hours bay No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Holding of "out of hours" specimens including blood cultures. 2) Refrigeration of "out of hours" specimens.
Personnel:
| Planning Relationships: | [5 empty] | Located to provide out of hours access whilst maintaining the security of the department.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 4 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Access to cross-matched blood "Out-of-hours".
| ADB | [7 empty] | Room Environmental Data
L0506
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0506 |  |  |  |  | Specimen hold: out-of-hours bay No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
Type Of Control:
Daytime General Service Illuminance (Lux):
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 96
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 96 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0506
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0506 |  |  |  |  | Specimen hold: out-of-hours bay No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0506
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0506 |  |  |  |  | Specimen hold: out-of-hours bay No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | LWB032 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 1200W 600D, HTM67 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LAB036 |  | INCUBATOR, variable temperature, 955H 640W 655D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF082 |  | REFRIGERATOR, blood, capacity 577 litres, single with temperature alarm system, external temperature gauge, 1995H 730W 800D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF066 |  | REFRIGERATOR, capacity 390 litres, 1855H 645W 595D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0510 |  |  |  |  | Blood bank area No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of blood from the Regional Blood Transfusion Service for storage prior to cross matching, storing blood transport boxes. 2) Reception of specimens from specimen reception. 3) Sorting, batching and labelling/numbering specimens and processing request forms. 4) Transferring batched specimens to main laboratory/bench/automated machine with request forms. 5) Displaying notices. 6) Storing transport boxes for blood.
| Personnel: | [6 empty] | Up to 2 staff
| Planning Relationships: | [5 empty] | Convenient access from entrance of department for receipt of blood supplies from the Regional Blood Transfusion Centre. Direct access to Blood Bank. Convenient access from Consultant's, Junior Medical staff, Head MLSO's, secretarial offices & departmental records.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Part of suite of rooms - Blood transfusion laboratory area.
| ADB | [7 empty] | Room Environmental Data
L0510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0510 |  |  |  |  | Blood bank area No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 97
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 97 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0510 |  |  |  |  | Blood bank area No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control, security control as necessary, see BS2881 Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0510 |  |  |  |  | Blood bank area No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 9 |  |  | 9 |  |  |  |  | SHE590 |  | SHELF, 1000W300D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SPI010 |  | SPINE UNIT, laboratory, 1000 length | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | WOR036 |  | WORKBENCH, laboratory, 920H 1000W 750D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | REF082 |  | REFRIGERATOR, blood, capacity 577 litres, single with temperature alarm system, external temperature gauge, 1995H 730W 800D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0513
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0513 |  |  |  |  | Laboratory: blood grouping No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Blood grouping (centrifuged, incubated, examined) specimens. 2) Examination of blood, for Rhesus antibody status. 3) Reading and recording results and writing reports. 4) Holding of "in use" reagents, solutions in small and large volumes disposables and small items of laboratory equipment. 5) Storage of samples/specimens under refrigerated/deep freeze conditions. 6) Displaying notices. 7) Holding of protective clothing for staff entering and leaving the laboratory area. 8) Clinical hand washing.
| Personnel: | [6 empty] | Up to 3 staff
| Planning Relationships: | [5 empty] | Direct access from Blood Transfusion Reception & to Cross-matching area. Convenient access from Consultant's, Junior Medical staff, Head MLSOs secretarial offices & departmental records.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Part of suite of rooms - Blood transfusion laboratory area.
| ADB | [7 empty] | Room Environmental Data
L0513
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0513 |  |  |  |  | Laboratory: blood grouping No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 98
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 98 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0513
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0513 |  |  |  |  | Laboratory: blood grouping No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0513
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0513 |  |  |  |  | Laboratory: blood grouping No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP444 |  | CUPBOARD, glass sliding doors, wall mounted, 600H 1000W 300D | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | DRA008 |  | DRAINAGE, catchpot | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWB052 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1200W 750D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWB080 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 2000W 750D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWS175 |  | WORKTOP, with sink on right (sink size 200x450x365), 920H 1500W 750D, HTM67 | [16 empty] | 1
| 14 |  |  | 14 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 11 |  |  | 11 |  |  |  |  | SHE590 |  | SHELF, 1000W300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SIN076 |  | SINK, inset, ceramic, 250H 500W 400D | [16 empty] | 1
| 15 |  |  | 15 |  |  |  |  | SPI010 |  | SPINE UNIT, laboratory, 1000 length | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP022 |  | TAP, laboratory, cold water | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | LAB036 |  | INCUBATOR, variable temperature, 955H 640W 655D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CEN003 |  | CENTRIFUGE bench mounted, 300H 420W 490D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CEN005 |  | CENTRIFUGE, cell washing (coomb's) bench mounted, 260H 260W 320D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CEN020 |  | CENTRIFUGE with microtiter head, 0-4000 RPM, bench mounted, 360H 490W 540D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CEN021 |  | CENTRIFUGE micro, high speed, 250H 305W340D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 5 |  |  | 5 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0513
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0513 |  |  |  |  | Laboratory: blood grouping No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB058 |  | MIXER, microtiter plate, 250H 650W 250D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB090 |  | BLOOD GROUPING SYSTEM automated, 700H 1250W 650D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB117 |  | BATH, water, electrothermal, 300H 325W 720D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC025 |  | MICROSCOPE, binocular, 300H 200W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF066 |  | REFRIGERATOR, capacity 390 litres, 1855H 645W 595D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0515
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0515 |  |  |  |  | Laboratory: blood cross-matching No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Blood and blood products are stored safely and securely. 2) Cross-matching blood including blood with abnormal antibodies. 3) Storing cross-matched blood. 4) Preparation of packed red cells. 5) Thawing fresh frozen plasma and cryoglobulin. 6) Reading and recording results and writing reports. 7) Holding of "in use" reagents, solutions in small and large volumes disposables and small items of laboratory equipment. 8) Storage of samples/specimens under refrigerated/deep freeze conditions. 9) Displaying notices. 10) Holding of protective clothing for staff entering and leaving the laboratory area. 11) Clinical hand washing.
| Personnel: | [6 empty] | Up to 3 staff
| Planning Relationships: | [5 empty] | Near to entrance of department for the collection of cross-matched blood. Direct access from Blood Transfusion Reception & Blood Grouping laboratory. Convenient access from Consultant's, Junior Medical staff, Head MLSO's, secretarial offices & departmental records.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Part of suite of rooms - Blood transfusion laboratory area. Storage of reagents to include sera.
| ADB | [7 empty] | Room Environmental Data
L0515
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0515 |  |  |  |  | Laboratory: blood cross-matching No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 99
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 99 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0515
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0515 |  |  |  |  | Laboratory: blood cross-matching No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0515
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0515 |  |  |  |  | Laboratory: blood cross-matching No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | CUP444 |  | CUPBOARD, glass sliding doors, wall mounted, 600H 1000W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | DRA008 |  | DRAINAGE, catchpot | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | LWB055 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1500W 750D, HTM67 | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | LWB075 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 1500W 750D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWB085 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 2500W 750D. | [16 empty] | 1
| 13 |  |  | 13 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | REF083 |  | REFRIGERATOR, blood with temperature alarm system, external temperature gauge, 1900H 1450W 800D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | REF087 |  | REFRIGERATOR, blood bank, external temperature gauge, underbench | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SHE590 |  | SHELF, 1000W300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SIN076 |  | SINK, inset, ceramic, 250H 500W 400D | [16 empty] | 1
| 13 |  |  | 13 |  |  |  |  | SPI010 |  | SPINE UNIT, laboratory, 1000 length | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP022 |  | TAP, laboratory, cold water | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP430 |  | TAP laboratory gas | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLO001 |  | CLOCK battery, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB036 |  | INCUBATOR, variable temperature, 955H 640W 655D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF082 |  | REFRIGERATOR, blood, capacity 577 litres, single with temperature alarm system, external temperature gauge, 1995H 730W 800D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF084 |  | REFRIGERATOR, blood, capacity 1245 litres, double with temperature alarm system, external temperature gauge, 1995H 1460W 800D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF122 |  | REFRIGERATOR/FREEZER, capacity 358 litres refrigerator, 143 litres freezer, 1700H 820W 720D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CEN005 |  | CENTRIFUGE, cell washing (coomb's) bench mounted, 260H 260W 320D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0515
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0515 |  |  |  |  | Laboratory: blood cross-matching No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CEN011 |  | CENTRIFUGE, refrigerated, bench mounted, 395H 640W 595D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CEN021 |  | CENTRIFUGE micro, high speed, 250H 305W340D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB025 |  | PLASMA EXTRACTOR, 270H 170W 260D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB117 |  | BATH, water, electrothermal, 300H 325W 720D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC025 |  | MICROSCOPE, binocular, 300H 200W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | OVE010 |  | OVEN, microwave, medium duty, 1600watt, capacity 26 litres, 370H 465W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0604
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0604 |  |  |  |  | Specialised laboratory: Containment level 3 No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from microbiology specimen reception, recording, sorting and batching of specimens. 2) Investigation of specimens to contain pathogens from hazard group 3. 3) Centrifugation and inoculation of samples (urine, blood, fluids) into solid or liquid culture media. 4) Staining of slide preparations. 5) Incubation under suitable temperature/environmental conditions. 6) Carrying out examination of specimens using a microscope. 7) Examination of incubated material. 8) Reading and recording results and writing reports. 9) Holding of "in use" reagents, flammable solvents, laboratory media and small items of equipment. 10) Storage of samples/specimens under refrigerated/deep freeze conditions. 11) Disposal of liquid waste. 12) Displaying notices.
| Personnel: | [6 empty] | Up to 2-3 staff; restricted access
| Planning Relationships: | [5 empty] | Access via lobby. Easy access for rapid & convenient transfer of specimens from Microbiology specimen reception bench. Easy access to Autoclave/wash-up area. Easy access from general Laboratory & Media preparation/plate pouring area. Near to Hot room. Convenient access from Consultant's, Junior Medical staff, Grade 3/4 technician's secretarial offices & departmental records. Sited away from main entrance of microbiology department.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | 2 No. Coat hook for protective white coats positioned in corridor outside door. Telephone - hands free is required. Pump vacuum is required.
| ADB | [7 empty] | Room Environmental Data
L0604
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0604 |  |  |  |  | Specialised laboratory: Containment level 3 No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG<BR>At all times.
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 100
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 100 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0604
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0604 |  |  |  |  | Specialised laboratory: Containment level 3 No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control, security control as necessary, see BS2881 Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0604
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0604 |  |  |  |  | Specialised laboratory: Containment level 3 No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | DRA008 |  | DRAINAGE, catchpot | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | EXT150 |  | EXTRACT, cabinet microbiological, exhaust protective class 1, BS5726 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWB052 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1200W 750D, HTM67 | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | LWB072 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 1200W 750D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWS175 |  | WORKTOP, with sink on right (sink size 200x450x365), 920H 1500W 750D, HTM67 | [16 empty] | 1
| 12 |  |  | 12 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 16 |  |  | 16 |  |  |  |  | SHE590 |  | SHELF, 1000W300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SIN076 |  | SINK, inset, ceramic, 250H 500W 400D | [16 empty] | 1
| 11 |  |  | 11 |  |  |  |  | SPI010 |  | SPINE UNIT, laboratory, 1000 length | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP022 |  | TAP, laboratory, cold water | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP060 |  | TAP laboratory water demineralised | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP430 |  | TAP laboratory gas | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP440 |  | TAP laboratory vacuum | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CAB072 |  | CABINET, exhaust protective, Class 1 microbiological safety BS5726, recirculating with integral fan and dual in line hepa filters,1420H 1200W 620D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB033 |  | BENCH MAGNIFIER, with fluorescent lamp, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | LAB036 |  | INCUBATOR, variable temperature, 955H 640W 655D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF122 |  | REFRIGERATOR/FREEZER, capacity 358 litres refrigerator, 143 litres freezer, 1700H 820W 720D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CEN019 |  | CENTRIFUGE, sealed buckets, adjustable speed, time and temp., mass 308kg; 30amp single phase, floor standing, mobile, 1140H 760W 990D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0604
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0604 |  |  |  |  | Specialised laboratory: Containment level 3 No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | HOL004 |  | HOLDER, sack, with lid foot operated, small, freestanding | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB009 |  | CANISTER, liquid nitrogen, capacity: 2 litres. Height without handle 270mm. Dia 145mm. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB021 |  | CABINET, slide dryer, 195H 437W 245D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB022 |  | SHAKING MACHINE, orbital, 125H 320W 375D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC023 |  | MICROSCOPE, fluorescence, 400H 225W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC025 |  | MICROSCOPE, binocular, 300H 200W 300D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0605
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0605 |  |  |  |  | Specialised laboratory: cell culture No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from specimen reception. 2) Sorting, batching and labelling/numbering specimens and processing request forms. 3) Transferring batched specimens to main laboratory/bench/automated machine with request forms. 4) Carrying out general bacteriological investigations, culture identification and sensitivity testing. 5) Centrifugation of samples/specimens (urine, blood, fluids). 6) Staining of slide preparations. 7) Carrying out examination of specimens using a microscope. 8) Preparing inoculated media for anaerobic investigation inc. evacuation of air from anaerobic jars and incubation under anaerobic conditions. 9) Incubation of culture media in special conditions (e.g. C02) and temperatures. 10) Notes and/or reports may be written. 11) Holding laboratory manuals, reference books. 12) Holding of "in use" reagents, flammable solvents, laboratory media and small items of equipment. 13) Storage of samples/specimens under refrigerated/deep freeze conditions. 14) Disposal of liquid waste. 15) Displaying notices. 16) Holding of protective clothing for staff entering and leaving the laboratory area. 17) Disposal of used protective clothing. 18) Clinical hand washing.
| Personnel: | [6 empty] | Up to 6 staff
| Planning Relationships: | [5 empty] | Easy access for rapid & convenient transfer of specimens from laboratory main specimen reception. Easy access to Containment Level III room & Autoclave/wash-up area. Close to Blood culture room, Bacterial & Viral Serology & Antibiotic section & the Media preparation/plate pouring areas. Near to Hot room. Convenient access from Consultant's Junior Medical staff, Head MLSO technician's, secretarial offices & departmental records.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Bacteriological investigations, culture identification & sensitivity testing mainly on the following: Urines, wound swabs, genito-urinary specimens & faeces (general microbiology) & on miscellaneous specimens e.g. cerebrospinal fluids & other fluids etc. includes: (a) plating & inoculation of appropriate culture media for isolation & identification of micro-organisms & antibiotic sensitivity testing, (b) making slides, examination of cultures, identification tests, sensitivity tests & recording results. Consideration of pipe runs from manifold for gases is required.
| ADB | [7 empty] | Room Environmental Data
L0605
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0605 |  |  |  |  | Specialised laboratory: cell culture No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 101
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 101 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0605
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0605 |  |  |  |  | Specialised laboratory: cell culture No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0605
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0605 |  |  |  |  | Specialised laboratory: cell culture No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CUP444 |  | CUPBOARD, glass sliding doors, wall mounted, 600H 1000W 300D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | LWB055 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1500W 750D, HTM67 | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | LWB075 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 1500W 750D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWB085 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 2500W 750D. | [16 empty] | 1
| 7 |  |  | 7 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 15 |  |  | 15 |  |  |  |  | SHE590 |  | SHELF, 1000W300D | [16 empty] | 1
| 9 |  |  | 9 |  |  |  |  | SPI010 |  | SPINE UNIT, laboratory, 1000 length | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP060 |  | TAP laboratory water demineralised | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP401 |  | TAP laboratory carbon dioxide | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP415 |  | TAP laboratory hydrogen | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP419 |  | TAP laboratory nitrogen | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP426 |  | TAP laboratory oxygen | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP429 |  | TAP laboratory argon | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | TAP430 |  | TAP laboratory gas | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB007 |  | FREEZER, -70 deg.C, floor standing, 1650H 1025W 1210D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB033 |  | BENCH MAGNIFIER, with fluorescent lamp, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB035 |  | INCUBATOR, carbon dioxide, bench mounted, 970H 630W 680D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB036 |  | INCUBATOR, variable temperature, 955H 640W 655D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB040 |  | GAS CHROMATOGRAPHY equipment, 463H 250W 363D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB119 |  | INCUBATOR, anaerobic chamber, 667H 1283W 700D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF103 |  | REFRIGERATED DEEP FREEZE, capacity 327 litres, vertical type, sparkfree interior, 1840H 660W 685D | [16 empty] | 2
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0605
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0605 |  |  |  |  | Specialised laboratory: cell culture No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAB042 |  | CABINET + cabinet dolly cart , bottle store, flammable liquids, mobile, 1040H 710W 485D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CEN017 |  | CENTRIFUGE, sealed buckets, mass 55kg, bench mounted, 340H 470W 550D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| 7 |  |  | 7 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB021 |  | CABINET, slide dryer, 195H 437W 245D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB024 |  | ROTARY PLATER, 100H 150W 155D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB034 |  | INOCULATOR, multi-point, 255H 410W 180D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB041 |  | DETECTOR, (to be used with Gas Chromatography equipment), 90H 270W 350D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB086 |  | COUNTER, colony, 90H 295W 325D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB117 |  | BATH, water, electrothermal, 300H 325W 720D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC020 |  | MICROSCOPE, inverted, 300H 200W 250D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC025 |  | MICROSCOPE, binocular, 300H 200W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF066 |  | REFRIGERATOR, capacity 390 litres, 1855H 645W 595D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0607
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0607 |  |  |  |  | Specialised laboratory: chromatography testing and mass spectroscopy No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Testing of specimens by special procedures for toxicology. 2) Testing of specimens by special procedures for chromatography. 3) Reading and recording results and writing reports. 4) Holding of "in use" reagents, solutions in small and large volumes disposables and small items of laboratory equipment. 5) Storage of samples/specimens under refrigerated/deep freeze conditions. 6) Displaying notices. 7) Holding of protective clothing for staff entering and leaving the laboratory area. 8) Disposal of used protective clothing. 9) Clinical hand washing.
| Personnel: | [6 empty] | Up to 3 staff
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Gas liquid chromatography (GLC) Thin layer chromatography (TLC)
| ADB | [7 empty] | Room Environmental Data
L0607
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0607 |  |  |  |  | Specialised laboratory: chromatography testing and mass spectroscopy No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 102
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 102 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0607
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0607 |  |  |  |  | Specialised laboratory: chromatography testing and mass spectroscopy No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Blinds are required. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0607
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0607 |  |  |  |  | Specialised laboratory: chromatography testing and mass spectroscopy No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO008 |  | HOOD, extract, 1800W 700D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP399 |  | TAP laboratory acetylene | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP415 |  | TAP laboratory hydrogen | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP419 |  | TAP laboratory nitrogen | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP426 |  | TAP laboratory oxygen | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP429 |  | TAP laboratory argon | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB040 |  | GAS CHROMATOGRAPHY equipment, 463H 250W 363D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF103 |  | REFRIGERATED DEEP FREEZE, capacity 327 litres, vertical type, sparkfree interior, 1840H 660W 685D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM046 |  | COMPUTER MONITOR, 15"; TFT, digital flat panel display, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB041 |  | DETECTOR, (to be used with Gas Chromatography equipment), 90H 270W 350D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB049 |  | THIN LAYER CHROMATOGRAPHY, equipment | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB050 |  | SCANNER, thin layer chromatography (TLC), 345H 620W 620D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF066 |  | REFRIGERATOR, capacity 390 litres, 1855H 645W 595D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SPE006 |  | SPECTROPHOTOMETER, Double beam UV/VIS | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SPE007 |  | SPECTROPHOTOMETER, ultra violet and recording, Microprocessor controlled single beam with touch screen, stores 50 methods and sets of date | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SPE008 |  | SPECTROPHOTOMETER, atomic absorption and printer | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0607
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0607 |  |  |  |  | Specialised laboratory: chromatography testing and mass spectroscopy No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0610
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0610 |  |  |  |  | Specialised laboratory: immunoassay testing No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Testing of specimens by special procedures on body fluids to monitor hormone imbalance, cancer and other tumour markers. 2) Testing of specimens by special procedures for steroids and drugs. 3) Testing of specimens by special procedures for protein. 4) Testing of specimens by special procedures for immuno-assay. 5) Reading and recording results and writing reports. 6) Holding of "in use" reagents, solutions in small and large volumes disposables and small items of laboratory equipment. 7) Storage of samples/specimens under refrigerated/deep freeze conditions. 8) Displaying notices. 9) Holding of protective clothing for staff entering and leaving the laboratory area. 10) Disposal of used protective clothing. 11) Clinical hand washing.
| Personnel: | [6 empty] | Up to 3 staff
| Planning Relationships: | [5 empty] | Easy access to General Laboratory. Easy access from Specimen Reception/Preparation & Preliminary Processing area/despatch area. Easy access to Chemical Store/Weighing/Reagent-solution Prep. area. Easy access to Cold room. Convenient access from Consultant's, Junior Medical staff, Grade 3/4 technician's, secretarial offices & departmental records.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Refrigerated storage to include reagents. Consideration of pipe runs from manifold for gases is required. Deionised water should be provided using resin based filter or points of use.
| ADB | [7 empty] | Room Environmental Data
L0610
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0610 |  |  |  |  | Specialised laboratory: immunoassay testing No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 103
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 103 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0610
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0610 |  |  |  |  | Specialised laboratory: immunoassay testing No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0610
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0610 |  |  |  |  | Specialised laboratory: immunoassay testing No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP145 |  | CUPBOARD, fume, separate extract and removable worktop floor standing, 2400H 1500W 900D | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | DRA008 |  | DRAINAGE, catchpot | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DRI021 |  | DRIP CUP, deck mounted | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 21 |  |  | 21 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 15 |  |  | 15 |  |  |  |  | SHE590 |  | SHELF, 1000W300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SIN076 |  | SINK, inset, ceramic, 250H 500W 400D | [16 empty] | 1
| 20 |  |  | 20 |  |  |  |  | SPI010 |  | SPINE UNIT, laboratory, 1000 length | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | TAP022 |  | TAP, laboratory, cold water | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP035 |  | TAP laboratory remote control extension spindle | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP060 |  | TAP laboratory water demineralised | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP430 |  | TAP laboratory gas | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | WOR022 |  | WORKBENCH, laboratory, 720H 1000W 750D | [16 empty] | 1
| 14 |  |  | 14 |  |  |  |  | WOR036 |  | WORKBENCH, laboratory, 920H 1000W 750D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | WOR043 |  | WORKBENCH, laboratory, 1000mm unit length, with cut-out for inset sink, 1000W 750D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CEN016 |  | CENTRIFUGE, refrigerated, floor standing, 1140H 760W 990D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | REF103 |  | REFRIGERATED DEEP FREEZE, capacity 327 litres, vertical type, sparkfree interior, 1840H 660W 685D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CEN012 |  | CENTRIFUGE, floor standing, mobile, 700H 670W 720D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0610
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0610 |  |  |  |  | Specialised laboratory: immunoassay testing No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 7 |  |  | 7 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP560 |  | CUPBOARD, metal, epoxy resin lined, flame resistant, lockable, 815H 760W 470D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB042 |  | FLUOROMETER, 175H 390W 310D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB046 |  | E.L.I.S.A. EQUIPMENT, dispenser (Enzyme linked immuno sorbent assay) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB047 |  | E.L.I.S.A. EQUIPMENT, washer (Enzyme linked immuno sorbent assay) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB048 |  | E.L.I.S.A. EQUIPMENT, plate reader (Enzyme linked immuno sorbent assay) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB051 |  | STIRRER, magnetic, 85H 225W 340D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB052 |  | MIXER, vortex | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB092 |  | BATH, water, electrothermal, boiling, with flat lid and rings | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0613
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0613 |  |  |  |  | Specialised laboratory: trace metal testing No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from chemical pathology reception or preparation area. 2) Carrying out preparation prior to testing specimens. 3) Testing of specimens by special procedures for trace metals. 4) Reading and recording results and writing reports. 5) Holding of "in use" reagents, solutions in small and large volumes disposables and small items of laboratory equipment. 6) Storage of samples/specimens under refrigerated/deep freeze conditions. 7) Displaying notices. 8) Holding of protective clothing for staff entering and leaving the laboratory area. 9) Disposal of used protective clothing. 10) Clinical hand washing.
Personnel:
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
L0613
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0613 |  |  |  |  | Specialised laboratory: trace metal testing No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 104
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 104 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0613
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0613 |  |  |  |  | Specialised laboratory: trace metal testing No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0613
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0613 |  |  |  |  | Specialised laboratory: trace metal testing No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF103 |  | REFRIGERATED DEEP FREEZE, capacity 327 litres, vertical type, sparkfree interior, 1840H 660W 685D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM046 |  | COMPUTER MONITOR, 15"; TFT, digital flat panel display, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF066 |  | REFRIGERATOR, capacity 390 litres, 1855H 645W 595D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0616
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0616 |  |  |  |  | Specialised laboratory: electrophoresis including PCR analysis No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Preparing samples for transmission electron microscopy (TEM) 2) Determining the electrophoretic mobility of protein and Hb in blood. 3) Reading and recording results and writing reports. 4) Holding of "in use" reagents, solutions in small and large volumes disposables and small items of laboratory equipment. 5) Storage of samples/specimens under refrigerated/deep freeze conditions. 6) Displaying notices. 7) Holding of protective clothing for staff entering and leaving the laboratory area. 8) Disposal of used protective clothing. 9) Clinical hand washing. 10) Emergency eye irrigation following contamination with corrosive or irritant substances.
Personnel:
| Planning Relationships: | [5 empty] | Located in close proximity to cold room & dark room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
L0616
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0616 |  |  |  |  | Specialised laboratory: electrophoresis including PCR analysis No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 105
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 105 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0616
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0616 |  |  |  |  | Specialised laboratory: electrophoresis including PCR analysis No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0616
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0616 |  |  |  |  | Specialised laboratory: electrophoresis including PCR analysis No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOT001 |  | BOTTLE, eye irrigation, emergency, with internal application, fix panel | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF103 |  | REFRIGERATED DEEP FREEZE, capacity 327 litres, vertical type, sparkfree interior, 1840H 660W 685D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BAL011 |  | BALANCER, electronic, 2 kg, 180H 60W 240D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB044 |  | ELECTROPHORESIS EQUIPMENT, power pack 120H 300W 280D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB045 |  | ELECTROPHORESIS EQUIPMENT, bath | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF066 |  | REFRIGERATOR, capacity 390 litres, 1855H 645W 595D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0618
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0618 |  |  |  |  | Specialised laboratory: flow cytometry No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Centrifugation of samples/specimens (urine, blood, fluids). 2) Notes and/or reports may be written. 3) Displaying notices. 4) Clinical hand washing.
Personnel:
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
L0618
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0618 |  |  |  |  | Specialised laboratory: flow cytometry No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 106
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 106 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0618
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0618 |  |  |  |  | Specialised laboratory: flow cytometry No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0618
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0618 |  |  |  |  | Specialised laboratory: flow cytometry No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DUC014 |  | DUCT, air extract | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CEN017 |  | CENTRIFUGE, sealed buckets, mass 55kg, bench mounted, 340H 470W 550D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF060 |  | REFRIGERATOR, reagents, capacity 110 litre, external temperature gauge, automatic defrost, underbench, 850H 500W 590D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0620
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0620 |  |  |  |  | Specialised laboratory: PCR sample preparation No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Preparing samples for polymerase chain reaction (PCR) testing. 2) Holding sterile and disposable items. 3) Disposal of single use items. 4) Emergency eye irrigation following contamination with corrosive or irritant substances. 5) Clinical hand washing.
Personnel:
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 10.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | PCR - Polymerase Chain Reaction
| ADB | [7 empty] | Room Environmental Data
L0620
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0620 |  |  |  |  | Specialised laboratory: PCR sample preparation No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 107
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 107 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0620
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0620 |  |  |  |  | Specialised laboratory: PCR sample preparation No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0620
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0620 |  |  |  |  | Specialised laboratory: PCR sample preparation No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOT001 |  | BOTTLE, eye irrigation, emergency, with internal application, fix panel | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CEN003 |  | CENTRIFUGE bench mounted, 300H 420W 490D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL008 |  | HOLDER, sack with lid foot operated, large, freestanding, 960H 500W 415D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0622
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0622 |  |  |  |  | Specialised laboratory: PCR setup No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Preparing samples for transmission electron microscopy (TEM) 2) Clinical hand washing.
Personnel:
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | PCR - Polymerase Chain Reaction Molecular biology techniques - A key technique is the polymerase chain reaction (PCR), which involves taking small quantities of a DNA molecule and creating millions of copies of it.
| ADB | [7 empty] | Room Environmental Data
L0622
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0622 |  |  |  |  | Specialised laboratory: PCR setup No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 108
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 108 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0622
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0622 |  |  |  |  | Specialised laboratory: PCR setup No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0622
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0622 |  |  |  |  | Specialised laboratory: PCR setup No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO009 |  | HOOD, extract, 1200W 500D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0701
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0701 |  |  |  |  | Laboratory: TEM sample preparation No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Preparing samples for transmission electron microscopy (TEM) 2) Preparing samples for polymerase chain reaction (PCR) testing. 3) Embedding processed tissue in resin. 4) Cutting sections of tissue embedded in resin. 5) Dispensing disposable gloves. 6) Disposal of used gowns. 7) Clinical hand washing.
Personnel:
| Planning Relationships: | [5 empty] | Close to darkroom. Close to office.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 10.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | TEM- Transmission Electron Microscopy, is used in diagnostic pathology for a number of processes including renal biopsy interpretation, investigation of myopathies and neuropathies, and virus identification.
| ADB | [7 empty] | Room Environmental Data
L0701
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0701 |  |  |  |  | Laboratory: TEM sample preparation No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 109
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 109 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0701
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0701 |  |  |  |  | Laboratory: TEM sample preparation No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0701
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0701 |  |  |  |  | Laboratory: TEM sample preparation No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP145 |  | CUPBOARD, fume, separate extract and removable worktop floor standing, 2400H 1500W 900D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWB012 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1200W 600D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS435 |  | DISPENSER, disposable gloves, set of 3, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB030 |  | OVEN, paraffin wax, 60 deg.C, includes stainless steel tapered wax container, 670H 640W 580D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB060 |  | ULTRA-MICROTOME, with integral stereo microscope, resin, thin section | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB063 |  | CONTROL UNIT for ultramicrotome (Part of LAB060) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF060 |  | REFRIGERATOR, reagents, capacity 110 litre, external temperature gauge, automatic defrost, underbench, 850H 500W 590D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO235 |  | TROLLEY, contaminated linen, single ring, stainless steel | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0703
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0703 |  |  |  |  | Laboratory: TEM microscope No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
Activities:
Personnel:
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | TEM- Transmission Electron Microscopy HBN Pathology Para 4.178The equipment is extremely sensitive to vibration and, although usually supplied with an antivibration table, is best located on a ground-bearing slab rather than a suspended slab on an upper floor.
| ADB | [7 empty] | Room Environmental Data
L0703
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0703 |  |  |  |  | Laboratory: TEM microscope No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 110
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 110 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0703
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0703 |  |  |  |  | Laboratory: TEM microscope No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - lightproof, outside release: 1 x personnel access (900mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0703
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0703 |  |  |  |  | Laboratory: TEM microscope No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0811
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0811 |  |  |  |  | Specimen reception: Histopathology, sorting, request processing Room layout in preparation
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Specimens are received and logged. 2) Visual display terminal(s) may be used. 3) Sorting, batching and labelling/numbering specimens and processing request forms. 4) Clinical hand washing.
| Personnel: | [6 empty] | Up to 3 staff
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Clock for recording receipt of specimens. Barcode reader/scanner with charging unit are require. Area should be separated into two areas: - booking of specimens - sorting and handling specimens
| ADB | [7 empty] | Room Environmental Data
L0811
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0811 |  |  |  |  | Specimen reception: Histopathology, sorting, request processing Room layout in preparation
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 500 |  | Over desk task area
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 111
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 111 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0811
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0811 |  |  |  |  | Specimen reception: Histopathology, sorting, request processing Room layout in preparation
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Essential Glazed sliding hatch, lockable Designation to be validated against current documentation
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0811
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0811 |  |  |  |  | Specimen reception: Histopathology, sorting, request processing Room layout in preparation
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL028 |  | BELL, call, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HAT017 |  | HATCH, vertical, sliding, 600W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWB012 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1200W 600D, HTM67 | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | LWB072 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 1200W 750D, HTM67 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLO004 |  | CLOCK battery with second sweep hand, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB033 |  | BENCH MAGNIFIER, with fluorescent lamp, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF103 |  | REFRIGERATED DEEP FREEZE, capacity 327 litres, vertical type, sparkfree interior, 1840H 660W 685D | [16 empty] | 2
| 3 |  |  | 3 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HEA010 |  | HEAT SEALING DEVICE, Includes paper guide, 150H 550W 250D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL008 |  | HOLDER, sack with lid foot operated, large, freestanding, 960H 500W 415D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | PRI017 |  | PRINTER bar code label, 230H 240W 370D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF067 |  | REFRIGERATOR, capacity 385 litre, automatic defrost, stainless steel, external temperature gauge, lockable, on castors, 1995H 600W 700D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0814
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0814 |  |  |  |  | Laboratory: Histopathology, specimen cut-up area No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from Histopathology specimen reception. 2) Preparation of tissue sections after specimen processing and gross cutting. 3) Cutting of tissue section from cooled wax blocks on a microtome. 4) Floating of tissue sections in a warm water bath and then mounting on a microscope slide. 5) Staining slides by mechanised machines or manually for routine or special techniques. 6) Applying manually or mechanically a glass coverslip over the section with styrene mounted and labelling slides. 7) Checking stained slides under microscope and labelling slides. 8) Investigation: Freezing portion of unfixed tissue and cutting sections in a cryostat from urgent specimens and routine immuno-histolog. techniques. 9) Frozen section investigation: Drying sections 10) Frozen section investigation: Staining sections. 11) Carrying out examination of specimens using a microscope. 12) Placing slides in a slide tray for despatch to pathologist. 13) Holding blocks and slides prior to dispatch for storage. 14) Transfer finished slides and blocks for storage. 15) Holding of "in use" reagents, solutions in small and large volumes disposables and small items of laboratory equipment. 16) Disposal of liquid waste. 17) Displaying notices. 18) Holding of protective clothing for staff entering and leaving the laboratory area. 19) Clinical hand washing.
| Personnel: | [6 empty] | Up to 5 staff
| Planning Relationships: | [5 empty] | Access via lobby at the entrance/exit to the room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | HISTOLOGY CUTTING ROUGH TRIMMING SET is required. CAMERA POLAROID is required.
| ADB | [7 empty] | Room Environmental Data
L0814
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0814 |  |  |  |  | Laboratory: Histopathology, specimen cut-up area No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG<BR>To circulation.POS Grasscuttig
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 112
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 112 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0814
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0814 |  |  |  |  | Laboratory: Histopathology, specimen cut-up area No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0814
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0814 |  |  |  |  | Laboratory: Histopathology, specimen cut-up area No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CAB041 |  | CABINET, specimen storage, ventilated, 200H 900W 900D | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG003 |  | LUMINAIRE, reading, adjustable arm, 100 watt | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP060 |  | TAP laboratory water demineralised | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP430 |  | TAP laboratory gas | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAS105 |  | WASTE DISPOSAL UNIT, sink waste | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | WOR037 |  | WORKBENCH laboratory stainless steel, downdraught, left hand plain top, with sink and disposal unit, 850H 1200W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 3 |  |  | 3 |  |  |  |  | DIC006 |  | DICTATING MACHINE, wall mounted, battery/mains operated | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 4 |  |  | 4 |  |  |  |  | LAB033 |  | BENCH MAGNIFIER, with fluorescent lamp, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BAL008 |  | BALANCE, analytical, 510g, 415H 240W 520D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | BAL011 |  | BALANCER, electronic, 2 kg, 180H 60W 240D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | BAL012 |  | BALANCER, electronic, 5 kg, 70H 20W 250D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HEA010 |  | HEAT SEALING DEVICE, Includes paper guide, 150H 550W 250D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LIG049 |  | PHOTOGRAPHIC LIGHTS SET | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MET005 |  | METER, pH., 190H 170L 260D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | MIC025 |  | MICROSCOPE, binocular, 300H 200W 300D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | MIC028 |  | MICROSCOPE, stereoscopic dissecting | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | STO023 |  | STOOL, laboratory, complete with footring | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO183 |  | TROLLEY, general purpose, 2 stainless steel shelves, 940H 970W 540D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0815
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0815 |  |  |  |  | Laboratory: Histopathology, specimen cut-up area including wet specimen store No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from Histopathology specimen reception. 2) Preparation of tissue sections after specimen processing and gross cutting. 3) Cutting of tissue section from cooled wax blocks on a microtome. 4) Floating of tissue sections in a warm water bath and then mounting on a microscope slide. 5) Slide labelling and drying in oven. 6) Dewaxing sections on slides prior to staining. 7) Staining slides by mechanised machines or manually for routine or special techniques. 8) Applying manually or mechanically a glass coverslip over the section with styrene mounted and labelling slides. 9) Checking stained slides under microscope and labelling slides. 10) Investigation: Freezing portion of unfixed tissue and cutting sections in a cryostat from urgent specimens and routine immuno-histolog. techniques. 11) Frozen section investigation: Drying sections 12) Frozen section investigation: Staining sections. 13) Carrying out examination of specimens using a microscope. 14) Placing slides in a slide tray for despatch to pathologist. 15) Holding blocks and slides prior to dispatch for storage. 16) Transfer finished slides and blocks for storage. 17) Storage of gross specimens in various sized containers during and for a variable period of time after processing. 18) Holding of "in use" reagents, solutions in small and large volumes disposables and small items of laboratory equipment. 19) Disposal of liquid waste. 20) Displaying notices. 21) Holding of protective clothing for staff entering and leaving the laboratory area. 22) Clinical hand washing.
| Personnel: | [6 empty] | Up to 5 staff
| Planning Relationships: | [5 empty] | Easy access from Histopathology specimen reception.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 42 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
L0815
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0815 |  |  |  |  | Laboratory: Histopathology, specimen cut-up area including wet specimen store No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG<BR>To circulation.POS Grasscuttig
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 113
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 113 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0815
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0815 |  |  |  |  | Laboratory: Histopathology, specimen cut-up area including wet specimen store No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0815
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0815 |  |  |  |  | Laboratory: Histopathology, specimen cut-up area including wet specimen store No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | CUP444 |  | CUPBOARD, glass sliding doors, wall mounted, 600H 1000W 300D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | DRA008 |  | DRAINAGE, catchpot | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO009 |  | HOOD, extract, 1200W 500D | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 16 |  |  | 16 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 12 |  |  | 12 |  |  |  |  | SHE590 |  | SHELF, 1000W300D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | TAP022 |  | TAP, laboratory, cold water | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP060 |  | TAP laboratory water demineralised | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP430 |  | TAP laboratory gas | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 10 |  |  | 10 |  |  |  |  | WOR037 |  | WORKBENCH laboratory stainless steel, downdraught, left hand plain top, with sink and disposal unit, 850H 1200W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA034 |  | BOARD, marker, whiteboard, dry-wipe, with pen holder, wall mounted, 600H 900W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB007 |  | FREEZER, -70 deg.C, floor standing, 1650H 1025W 1210D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | LAB031 |  | OVEN, hot air, low temperature, 920H 962W 898D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF122 |  | REFRIGERATOR/FREEZER, capacity 358 litres refrigerator, 143 litres freezer, 1700H 820W 720D | [16 empty] | 2
| 5 |  |  | 5 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 7 |  |  | 7 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CYL003 |  | CYLINDER carbon dioxide, type C, 450 litres, small, 356H 89 dia. | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0815
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0815 |  |  |  |  | Laboratory: Histopathology, specimen cut-up area including wet specimen store No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 4 |  |  | 4 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL008 |  | HOLDER, sack with lid foot operated, large, freestanding, 960H 500W 415D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | LAB002 |  | BATH, floating off, pilot light, thermostat, thermometer holder. | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | LAB003 |  | COOLER PLATE, wax block | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB004 |  | DEEP FREEZER, bench mounted | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB070 |  | CRYOSTAT, freezing microtome, 1420H 660W 760D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB078 |  | MACHINE, slide drying, linear, 155H 1050W 155D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB085 |  | COVERSLIPPING MACHINE, mechanical, 610H 360W 420D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | LAB120 |  | MICROTOME, sledge, 350H 200W 550D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC025 |  | MICROSCOPE, binocular, 300H 200W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC026 |  | MICROSCOPE, polarising, 300H 200W 250D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0817
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0817 |  |  |  |  | Laboratory: Histopathology, high risk specimen cut-up area With safety cabinet class 1 No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from Histopathology specimen reception. 2) Processing of specimens which need to be within a microbiological safety cabinet (Class 1). 3) Holding blocks and slides prior to dispatch for storage. 4) Transfer finished slides and blocks for storage. 5) Holding of "in use" reagents, solutions in small and large volumes disposables and small items of laboratory equipment. 6) Disposal of liquid waste. 7) Displaying notices. 8) Holding of protective clothing for staff entering and leaving the laboratory area. 9) Clinical hand washing.
| Personnel: | [6 empty] | 1 - 2 staff
| Planning Relationships: | [5 empty] | Access via lobby. Direct access via lobby to histology specimen cut up area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 10.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | HISTOLOGY CUTTING ROUGH TRIMMING SET is required.
| ADB | [7 empty] | Room Environmental Data
L0817
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0817 |  |  |  |  | Laboratory: Histopathology, high risk specimen cut-up area With safety cabinet class 1 No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG<BR>To circulation.POS Grasscuttig
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 114
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 114 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0817
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0817 |  |  |  |  | Laboratory: Histopathology, high risk specimen cut-up area With safety cabinet class 1 No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0817
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0817 |  |  |  |  | Laboratory: Histopathology, high risk specimen cut-up area With safety cabinet class 1 No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAB041 |  | CABINET, specimen storage, ventilated, 200H 900W 900D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | EXT150 |  | EXTRACT, cabinet microbiological, exhaust protective class 1, BS5726 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG003 |  | LUMINAIRE, reading, adjustable arm, 100 watt | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWB075 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 1500W 750D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WOR037 |  | WORKBENCH laboratory stainless steel, downdraught, left hand plain top, with sink and disposal unit, 850H 1200W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB072 |  | CABINET, exhaust protective, Class 1 microbiological safety BS5726, recirculating with integral fan and dual in line hepa filters,1420H 1200W 620D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIC006 |  | DICTATING MACHINE, wall mounted, battery/mains operated | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB033 |  | BENCH MAGNIFIER, with fluorescent lamp, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | WAS051 |  | WASH, eye, first aid, with mirror, wall mounted, 360H 250W 100D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BAL011 |  | BALANCER, electronic, 2 kg, 180H 60W 240D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP560 |  | CUPBOARD, metal, epoxy resin lined, flame resistant, lockable, 815H 760W 470D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HEA010 |  | HEAT SEALING DEVICE, Includes paper guide, 150H 550W 250D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MET005 |  | METER, pH., 190H 170L 260D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0817
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0817 |  |  |  |  | Laboratory: Histopathology, high risk specimen cut-up area With safety cabinet class 1 No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | MIC028 |  | MICROSCOPE, stereoscopic dissecting | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STO023 |  | STOOL, laboratory, complete with footring | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO183 |  | TROLLEY, general purpose, 2 stainless steel shelves, 940H 970W 540D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0818
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0818 |  |  |  |  | Laboratory: Histopathology, processing No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Mechanised processing of specimens of tissues. 2) Embedding processed tissue in paraffin wax. 3) Short term storage of specimens. 4) Storage of gross specimens in various sized containers during and for a variable period of time after processing. 5) Mounting prepared tissue for demonstration and the preparation of specimen and tissue, in plastic bags (heat sealed) for prolonged storage. 6) Storing supply of stock materials and control positive tissue. 7) Storing disposable gloves, aprons, instruments, packs of cassettes and manuals for equipment. 8) Holding of protective clothing for staff entering and leaving the laboratory area. 9) Clinical hand washing.
| Personnel: | [6 empty] | Up to 3 staff
| Planning Relationships: | [5 empty] | Easy access from laboratory specimen reception. Adjacent to cut-up room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Telephone outlet with `hands off' facility. Deionised water should be provided using resin based filter or points of use.
| ADB | [7 empty] | Room Environmental Data
L0818
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0818 |  |  |  |  | Laboratory: Histopathology, processing No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 115
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 115 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0818
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0818 |  |  |  |  | Laboratory: Histopathology, processing No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0818
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0818 |  |  |  |  | Laboratory: Histopathology, processing No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DRA008 |  | DRAINAGE, catchpot | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU013 |  | DISPOSAL UNIT, hopper with flushing rim, 110mm outlet, no tap holes no overflow, back inlet, stainless steel, 900H 600W 600D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWB090 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 3000W 750D, HTM67 | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT345 |  | OUTLET, floor drainage and grating, 150 mm dia. hospital pattern. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO002 |  | SHOWER, slip resistant floor with drainage outlet, 900W 900D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO025 |  | DRENCH SHOWER chain operated | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SIN081 |  | SINK, inset, stainless steel, 250H 500W 400D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP001 |  | TAP extension piece(bib/pillar), length to suit | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | TAP022 |  | TAP, laboratory, cold water | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP023 |  | TAP, laboratory, hot water | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP060 |  | TAP laboratory water demineralised | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | WAS105 |  | WASTE DISPOSAL UNIT, sink waste | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | WOR037 |  | WORKBENCH laboratory stainless steel, downdraught, left hand plain top, with sink and disposal unit, 850H 1200W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIC006 |  | DICTATING MACHINE, wall mounted, battery/mains operated | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB033 |  | BENCH MAGNIFIER, with fluorescent lamp, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | WAS051 |  | WASH, eye, first aid, with mirror, wall mounted, 360H 250W 100D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB042 |  | CABINET + cabinet dolly cart , bottle store, flammable liquids, mobile, 1040H 710W 485D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CAB115 |  | CABINET chemical storage, underbench, lockable, 500H 400W 600D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HEA010 |  | HEAT SEALING DEVICE, Includes paper guide, 150H 550W 250D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0818
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0818 |  |  |  |  | Laboratory: Histopathology, processing No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL008 |  | HOLDER, sack with lid foot operated, large, freestanding, 960H 500W 415D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | LAB016 |  | TISSUE PROCESSOR ENCLOSED MODULAR, 1360H 600W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB069 |  | DECALCIFYING AGITATOR, 300H 300 dia. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0819
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0819 |  |  |  |  | Store: Histopathology, wet specimen No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Sorting, batching and labelling/numbering specimens and processing request forms. 2) Transferring batched specimens to main laboratory/bench/automated machine with request forms. 3) Short term storage of specimens. 4) Storage of gross specimens in various sized containers during and for a variable period of time after processing. 5) Storing disposable gloves, aprons, instruments, packs of cassettes and manuals for equipment. 6) Displaying notices. 7) Clinical hand washing.
| Personnel: | [6 empty] | Up to 3 staff
| Planning Relationships: | [5 empty] | Easy access for rapid & convenient transfer of specimens from laboratory Main specimen reception. Direct access to general laboratory. Near to Chemical store/preparation area. Convenient access from Consultant's, Junior Medical staff, Head MLSO's, secretarial offices & departmental records.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 10.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Telephone outlet with `hands off' facility.
| ADB | [7 empty] | Room Environmental Data
L0819
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0819 |  |  |  |  | Store: Histopathology, wet specimen No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 116
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 116 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0819
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0819 |  |  |  |  | Store: Histopathology, wet specimen No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0819
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0819 |  |  |  |  | Store: Histopathology, wet specimen No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWB012 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1200W 600D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE241 |  | SHELF, 1800W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE242 |  | SHELF, 1800W 400D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE251 |  | SHELF, 2100W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE252 |  | SHELF, 2100W 400D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP022 |  | TAP, laboratory, cold water | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP060 |  | TAP laboratory water demineralised | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WOR037 |  | WORKBENCH laboratory stainless steel, downdraught, left hand plain top, with sink and disposal unit, 850H 1200W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLO001 |  | CLOCK battery, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIC006 |  | DICTATING MACHINE, wall mounted, battery/mains operated | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF103 |  | REFRIGERATED DEEP FREEZE, capacity 327 litres, vertical type, sparkfree interior, 1840H 660W 685D | [16 empty] | 2
| 5 |  |  | 5 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HEA010 |  | HEAT SEALING DEVICE, Includes paper guide, 150H 550W 250D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0819
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0819 |  |  |  |  | Store: Histopathology, wet specimen No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | HOL008 |  | HOLDER, sack with lid foot operated, large, freestanding, 960H 500W 415D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF066 |  | REFRIGERATOR, capacity 390 litres, 1855H 645W 595D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | SCA125 |  | SCALE, 5 kg | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0821
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0821 |  |  |  |  | Laboratory: Histopathology, general and special including resin work No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from Histopathology specimen reception. 2) Preparation of tissue sections after specimen processing and gross cutting. 3) Cutting of tissue section from cooled wax blocks on a microtome. 4) Floating of tissue sections in a warm water bath and then mounting on a microscope slide. 5) Resin work: a) Section cutting, b) section staining, c) section mounting. 6) Slide labelling and drying in oven. 7) Dewaxing sections on slides prior to staining. 8) Staining slides by mechanised machines or manually for routine or special techniques. 9) Applying manually or mechanically a glass coverslip over the section with styrene mounted and labelling slides. 10) Checking stained slides under microscope and labelling slides. 11) Investigation: Freezing portion of unfixed tissue and cutting sections in a cryostat from urgent specimens and routine immuno-histolog. techniques. 12) Frozen section investigation: Drying sections 13) Frozen section investigation: Staining sections. 14) Carrying out examination of specimens using a microscope. 15) Placing slides in a slide tray for despatch to pathologist. 16) Holding blocks and slides prior to dispatch for storage. 17) Transfer finished slides and blocks for storage. 18) Holding of "in use" reagents, solutions in small and large volumes disposables and small items of laboratory equipment. 19) Disposal of liquid waste. 20) Holding of protective clothing for staff entering and leaving the laboratory area. 21) Clinical hand washing.
| Personnel: | [6 empty] | Up to 5 staff
| Planning Relationships: | [5 empty] | Easy access from Histopathology specimen reception bench.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 126 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Associated with Cytopathology processing & screening. Deionised water should be provided using resin based filter or points of use. Flammable material stored elsewhere.
| ADB | [7 empty] | Room Environmental Data
L0821
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0821 |  |  |  |  | Laboratory: Histopathology, general and special including resin work No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG<BR>To circulation.POS Grasscuttig
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 117
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 117 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0821
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0821 |  |  |  |  | Laboratory: Histopathology, general and special including resin work No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0821
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0821 |  |  |  |  | Laboratory: Histopathology, general and special including resin work No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 6 |  |  | 6 |  |  |  |  | LWB090 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 3000W 750D, HTM67 | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | LWS175 |  | WORKTOP, with sink on right (sink size 200x450x365), 920H 1500W 750D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT345 |  | OUTLET, floor drainage and grating, 150 mm dia. hospital pattern. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | REF031 |  | FREEZER underbench -20 deg.C, 905H 600W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO002 |  | SHOWER, slip resistant floor with drainage outlet, 900W 900D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO025 |  | DRENCH SHOWER chain operated | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP060 |  | TAP laboratory water demineralised | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP430 |  | TAP laboratory gas | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAS110 |  | *BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, concealed waste, 500W 400D. HTM64LBHM. Replaced by: BAS101, 15/05/06 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO001 |  | CLOCK battery, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CUP149 |  | CUPBOARD, fume, bench mounted, 1145H 1200W 570D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB007 |  | FREEZER, -70 deg.C, floor standing, 1650H 1025W 1210D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB036 |  | INCUBATOR, variable temperature, 955H 640W 655D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | WAS051 |  | WASH, eye, first aid, with mirror, wall mounted, 360H 250W 100D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BAL004 |  | BALANCE, top pan, capacity 101g, 300H 300W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CAB042 |  | CABINET + cabinet dolly cart , bottle store, flammable liquids, mobile, 1040H 710W 485D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CAB052 |  | CABINET, slide storage, 14 drawer, capacity 6000 slides, 140H 480W 480D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP560 |  | CUPBOARD, metal, epoxy resin lined, flame resistant, lockable, 815H 760W 470D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0821
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0821 |  |  |  |  | Laboratory: Histopathology, general and special including resin work No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | LAB002 |  | BATH, floating off, pilot light, thermostat, thermometer holder. | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | LAB003 |  | COOLER PLATE, wax block | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB011 |  | CABINET, block storage (wax embedded tissue), 10 drawer, 282H 480W 480D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB013 |  | MACHINE, TISSUE EMBEDDING CENTRE, wax | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB015 |  | EMBEDDING CENTRE AUTOMATED, 1400H 750W 1370D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB020 |  | SLIDE WARMER, 60H 270W 400D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB021 |  | CABINET, slide dryer, 195H 437W 245D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | LAB037 |  | HOT PLATE, 85H 225W 340D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB070 |  | CRYOSTAT, freezing microtome, 1420H 660W 760D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB085 |  | COVERSLIPPING MACHINE, mechanical, 610H 360W 420D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | LAB094 |  | BATH, floating off, 115H 340W 230D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB104 |  | IMMUNOSTAINER, 703H 760W 775D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB106 |  | STAINING MACHINE for slides, 24 station, with heater and monitor, 600H 760 dia. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB107 |  | STAINER SLIDE LINEAR AUTO, 300H 150W 1500D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | LAB117 |  | BATH, water, electrothermal, 300H 325W 720D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB120 |  | MICROTOME, sledge, 350H 200W 550D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB121 |  | MICROTOME ROTARY, 300H 470W 400D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB124 |  | HOTPLATE/STIRRER, 150H 250W 250D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB129 |  | OVEN wax explosion proof, 700H 550W 650D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MET005 |  | METER, pH., 190H 170L 260D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC022 |  | MICROSCOPE, binocular fluorescent, 650H 550W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC025 |  | MICROSCOPE, binocular, 300H 200W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC030 |  | MICROSCOPE, dual head, 450H 500W 800D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | OVE010 |  | OVEN, microwave, medium duty, 1600watt, capacity 26 litres, 370H 465W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | PRI021 |  | PRINTER slide auto, 940H 650W 460H | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | PRI023 |  | PRINTER cassette, 940H 650W 460D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | REF066 |  | REFRIGERATOR, capacity 390 litres, 1855H 645W 595D | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | STO023 |  | STOOL, laboratory, complete with footring | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0822
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0822 |  |  |  |  | Laboratory: Histopathology, general No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from Histopathology specimen reception. 2) Preparation of tissue sections after specimen processing and gross cutting. 3) Cutting of tissue section from cooled wax blocks on a microtome. 4) Floating of tissue sections in a warm water bath and then mounting on a microscope slide. 5) Slide labelling and drying in oven. 6) Dewaxing sections on slides prior to staining. 7) Staining slides by mechanised machines or manually for routine or special techniques. 8) Applying manually or mechanically a glass coverslip over the section with styrene mounted and labelling slides. 9) Checking stained slides under microscope and labelling slides. 10) Investigation: Freezing portion of unfixed tissue and cutting sections in a cryostat from urgent specimens and routine immuno-histolog. techniques. 11) Frozen section investigation: Drying sections 12) Frozen section investigation: Staining sections. 13) Carrying out examination of specimens using a microscope. 14) Placing slides in a slide tray for despatch to pathologist. 15) Holding blocks and slides prior to dispatch for storage. 16) Transfer finished slides and blocks for storage. 17) Holding of "in use" reagents, solutions in small and large volumes disposables and small items of laboratory equipment. 18) Disposal of liquid waste. 19) Displaying notices. 20) Holding of protective clothing for staff entering and leaving the laboratory area. 21) Clinical hand washing.
| Personnel: | [6 empty] | Up to 5 staff
| Planning Relationships: | [5 empty] | Easy access for rapid & convenient transfer of specimens from Histopathology specimen reception bench. Easy access from Gross Cutting, Specimen processing/specimen storage room. Easy access to Slide/block store. Easy access to laboratory store & chemical store/preparation area. Convenient access from Consultant's, Junior Medical staff, Head MLSO's, secretarial offices & departmental records.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 94.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Associated with Cytopathology processing & screening. Flammable material stored elsewhere.
| ADB | [7 empty] | Room Environmental Data
L0822
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0822 |  |  |  |  | Laboratory: Histopathology, general No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG<BR>To circulation.POS Grasscuttig
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 118
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 118 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0822
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0822 |  |  |  |  | Laboratory: Histopathology, general No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0822
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0822 |  |  |  |  | Laboratory: Histopathology, general No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | LWB090 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 3000W 750D, HTM67 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWS175 |  | WORKTOP, with sink on right (sink size 200x450x365), 920H 1500W 750D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT345 |  | OUTLET, floor drainage and grating, 150 mm dia. hospital pattern. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | REF031 |  | FREEZER underbench -20 deg.C, 905H 600W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO002 |  | SHOWER, slip resistant floor with drainage outlet, 900W 900D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO025 |  | DRENCH SHOWER chain operated | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP060 |  | TAP laboratory water demineralised | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP430 |  | TAP laboratory gas | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLO001 |  | CLOCK battery, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB007 |  | FREEZER, -70 deg.C, floor standing, 1650H 1025W 1210D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP560 |  | CUPBOARD, metal, epoxy resin lined, flame resistant, lockable, 815H 760W 470D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | LAB002 |  | BATH, floating off, pilot light, thermostat, thermometer holder. | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | LAB003 |  | COOLER PLATE, wax block | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB011 |  | CABINET, block storage (wax embedded tissue), 10 drawer, 282H 480W 480D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB013 |  | MACHINE, TISSUE EMBEDDING CENTRE, wax | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB015 |  | EMBEDDING CENTRE AUTOMATED, 1400H 750W 1370D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB020 |  | SLIDE WARMER, 60H 270W 400D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0822
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0822 |  |  |  |  | Laboratory: Histopathology, general No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | LAB021 |  | CABINET, slide dryer, 195H 437W 245D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | LAB037 |  | HOT PLATE, 85H 225W 340D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB070 |  | CRYOSTAT, freezing microtome, 1420H 660W 760D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB085 |  | COVERSLIPPING MACHINE, mechanical, 610H 360W 420D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | LAB094 |  | BATH, floating off, 115H 340W 230D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB104 |  | IMMUNOSTAINER, 703H 760W 775D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB106 |  | STAINING MACHINE for slides, 24 station, with heater and monitor, 600H 760 dia. | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB107 |  | STAINER SLIDE LINEAR AUTO, 300H 150W 1500D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | LAB117 |  | BATH, water, electrothermal, 300H 325W 720D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB120 |  | MICROTOME, sledge, 350H 200W 550D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | LAB121 |  | MICROTOME ROTARY, 300H 470W 400D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB124 |  | HOTPLATE/STIRRER, 150H 250W 250D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB129 |  | OVEN wax explosion proof, 700H 550W 650D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC022 |  | MICROSCOPE, binocular fluorescent, 650H 550W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC025 |  | MICROSCOPE, binocular, 300H 200W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC030 |  | MICROSCOPE, dual head, 450H 500W 800D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | PRI021 |  | PRINTER slide auto, 940H 650W 460H | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | PRI023 |  | PRINTER cassette, 940H 650W 460D | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | STO023 |  | STOOL, laboratory, complete with footring | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0823
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0823 |  |  |  |  | Laboratory: Histopathology, resin work No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from Histopathology specimen reception. 2) Resin work: a) Section cutting, b) section staining, c) section mounting. 3) Histochemistry: Immunocytochemistry, Immunofluorescence and Crystallography - Slides received from general laboratory. 4) Histochemistry: Immunocytochemistry, Immunofluorescence and Crystallography - Slides treated with anti-sera and dyes. 5) Carrying out examination of specimens using a microscope. 6) Holding of "in use" reagents, flammable solvents, laboratory media and small items of equipment. 7) Disposal of liquid waste. 8) Displaying notices. 9) Holding of protective clothing for staff entering and leaving the laboratory area. 10) Clinical hand washing.
| Personnel: | [6 empty] | 1 x Person
| Planning Relationships: | [5 empty] | Easy access for rapid & convenient transfer of specimens from Histopathology specimen reception bench. Easy access from Gross Cutting, Specimen processing/specimen storage room. Easy access to Slide/block store. Easy access to laboratory store & chemical store/preparation area. Convenient access from Consultant's, Junior Medical staff, Head MLSO's, secretarial offices & departmental records.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Associated with Cytopathology processing & screening. Deionised water should be provided using resin based filter or points of use. Flammable material stored elsewhere.
| ADB | [7 empty] | Room Environmental Data
L0823
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0823 |  |  |  |  | Laboratory: Histopathology, resin work No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 119
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 119 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0823
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0823 |  |  |  |  | Laboratory: Histopathology, resin work No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0823
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0823 |  |  |  |  | Laboratory: Histopathology, resin work No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CUP444 |  | CUPBOARD, glass sliding doors, wall mounted, 600H 1000W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG003 |  | LUMINAIRE, reading, adjustable arm, 100 watt | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWB052 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1200W 750D, HTM67 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWB075 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 1500W 750D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWS175 |  | WORKTOP, with sink on right (sink size 200x450x365), 920H 1500W 750D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLO001 |  | CLOCK battery, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CUP149 |  | CUPBOARD, fume, bench mounted, 1145H 1200W 570D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB033 |  | BENCH MAGNIFIER, with fluorescent lamp, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | WAS051 |  | WASH, eye, first aid, with mirror, wall mounted, 360H 250W 100D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL004 |  | HOLDER, sack, with lid foot operated, small, freestanding | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB017 |  | TISSUE PROCESSOR bench top electron microscopt (EM), 300H 420W 520D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0823
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0823 |  |  |  |  | Laboratory: Histopathology, resin work No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | LAB060 |  | ULTRA-MICROTOME, with integral stereo microscope, resin, thin section | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB063 |  | CONTROL UNIT for ultramicrotome (Part of LAB060) | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB064 |  | CRYO SUPPLY UNIT with hose attachment, mobile | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB065 |  | MIXER rotary vertical type, 800H 750W 360D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB095 |  | BATH, ultrasonic cleaner, includes basket and stainless steel lid, heated, 200H 300W 240D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB105 |  | STAINER SECTION AUTOMATIC bench top (EM), 350H 500W 400D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB123 |  | HOTPLATE three temperature (EM), 100H 200W 150D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB131 |  | OVEN curing resin, 500H 450W 400D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB195 |  | KNIFE maker glass balaced (EM), 300H 330W 400D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB200 |  | VACUUM EVAPORATOR bench top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB201 |  | ETCHER VACUUM COATER complete, (Plasma etching system), 300H 450W 350D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB202 |  | PUMP VACUUM rotary, 250H 350W 250D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB205 |  | TRIMMER specimen (EM), 400H 450W 400D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB207 |  | PLATE VIBRATION absorbing, 70H 500W 420D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MIC025 |  | MICROSCOPE, binocular, 300H 200W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF120 |  | REFRIGERATOR/FREEZER, capacity 160 litre refrigerator, 126 litre freezer, 1650H 550W 610D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0826
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0826 |  |  |  |  | Store: Histopathology, slide and block No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Storing histopathology slides and blocks.
| Personnel: | [6 empty] | 1 x Staff
| Planning Relationships: | [5 empty] | Convenient access to laboratories served.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Long term storage is provided off-site the department.
| ADB | [7 empty] | Room Environmental Data
L0826
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0826 |  |  |  |  | Store: Histopathology, slide and block No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 120
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 120 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0826
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0826 |  |  |  |  | Store: Histopathology, slide and block No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0826
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0826 |  |  |  |  | Store: Histopathology, slide and block No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 10 |  |  | 10 |  |  |  |  | CAB052 |  | CABINET, slide storage, 14 drawer, capacity 6000 slides, 140H 480W 480D | [16 empty] | 3
| 10 |  |  | 10 |  |  |  |  | LAB011 |  | CABINET, block storage (wax embedded tissue), 10 drawer, 282H 480W 480D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0828
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0828 |  |  |  |  | Store and chemical preparation area: Histopathology No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Storing chemicals. 2) Preparing solutions and stains. 3) Clinical hand washing.
| Personnel: | [6 empty] | Up to 2 staff
| Planning Relationships: | [5 empty] | Easy access to areas served.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
L0828
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0828 |  |  |  |  | Store and chemical preparation area: Histopathology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 121
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 121 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0828
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0828 |  |  |  |  | Store and chemical preparation area: Histopathology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0828
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0828 |  |  |  |  | Store and chemical preparation area: Histopathology No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | DRA008 |  | DRAINAGE, catchpot | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWB085 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 2500W 750D. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | LWS175 |  | WORKTOP, with sink on right (sink size 200x450x365), 920H 1500W 750D, HTM67 | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP022 |  | TAP, laboratory, cold water | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP149 |  | CUPBOARD, fume, bench mounted, 1145H 1200W 570D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DEI001 |  | DEIONISER, water, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB110 |  | STILL, distilled water, 8l/hr, wall mounted, 410H 550W 240D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | WAS051 |  | WASH, eye, first aid, with mirror, wall mounted, 360H 250W 100D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BAL003 |  | BALANCE, top plan, capacity 4500g, increments 0.01g, 130H 185W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | BAL008 |  | BALANCE, analytical, 510g, 415H 240W 520D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP560 |  | CUPBOARD, metal, epoxy resin lined, flame resistant, lockable, 815H 760W 470D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL008 |  | HOLDER, sack with lid foot operated, large, freestanding, 960H 500W 415D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB037 |  | HOT PLATE, 85H 225W 340D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB051 |  | STIRRER, magnetic, 85H 225W 340D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0828
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0828 |  |  |  |  | Store and chemical preparation area: Histopathology No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | LAB117 |  | BATH, water, electrothermal, 300H 325W 720D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | MET005 |  | METER, pH., 190H 170L 260D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0830
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0830 |  |  |  |  | Laboratory: Histopathology, urgent frozen section No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from Histopathology specimen reception. 2) Disposal of liquid waste. 3) Displaying notices. 4) Holding of protective clothing for staff entering and leaving the laboratory area. 5) Clinical hand washing.
| Personnel: | [6 empty] | 1 x Person
| Planning Relationships: | [5 empty] | Easy access for rapid & convenient transfer of specimens from Histopathology specimen reception bench. Easy access from Gross Cutting, Specimen processing/specimen storage room. Easy access to Slide/block store. Easy access to laboratory store & chemical store/preparation area. Convenient access from Consultant's, Junior Medical staff, Head MLSO's, secretarial offices & departmental records.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
L0830
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0830 |  |  |  |  | Laboratory: Histopathology, urgent frozen section No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 122
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 122 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0830
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0830 |  |  |  |  | Laboratory: Histopathology, urgent frozen section No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0830
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0830 |  |  |  |  | Laboratory: Histopathology, urgent frozen section No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CUP444 |  | CUPBOARD, glass sliding doors, wall mounted, 600H 1000W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | LWB055 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1500W 750D, HTM67 | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | LWB090 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 3000W 750D, HTM67 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWS175 |  | WORKTOP, with sink on right (sink size 200x450x365), 920H 1500W 750D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | SHE590 |  | SHELF, 1000W300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOT001 |  | BOTTLE, eye irrigation, emergency, with internal application, fix panel | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | REF103 |  | REFRIGERATED DEEP FREEZE, capacity 327 litres, vertical type, sparkfree interior, 1840H 660W 685D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB042 |  | CABINET + cabinet dolly cart , bottle store, flammable liquids, mobile, 1040H 710W 485D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA051 |  | DRAWER UNIT, 5 drawer, on castors, 600H 500W 500D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL004 |  | HOLDER, sack, with lid foot operated, small, freestanding | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB060 |  | ULTRA-MICROTOME, with integral stereo microscope, resin, thin section | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0830
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0830 |  |  |  |  | Laboratory: Histopathology, urgent frozen section No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OVE010 |  | OVEN, microwave, medium duty, 1600watt, capacity 26 litres, 370H 465W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0903
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0903 |  |  |  |  | Specimen reception: Cytopathology No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Specimens are received and logged. 2) Visual display terminal(s) may be used. 3) Sorting, batching and labelling/numbering specimens and processing request forms.
| Personnel: | [6 empty] | Up to 3 staff
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 42 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Clock for recording receipt of specimens. Barcode reader/scanner with charging unit are require. Area should be separated into two areas: - booking of specimens - sorting and handling specimens
| ADB | [7 empty] | Room Environmental Data
L0903
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0903 |  |  |  |  | Specimen reception: Cytopathology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 123
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 123 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0903
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0903 |  |  |  |  | Specimen reception: Cytopathology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Essential Glazed sliding hatch, lockable Designation to be validated against current documentation
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0903
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0903 |  |  |  |  | Specimen reception: Cytopathology No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL028 |  | BELL, call, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | COU001 |  | COUNTER RECEPTION, design and fitting project specific | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HAT017 |  | HATCH, vertical, sliding, 600W 300D | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWB012 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1200W 600D, HTM67 | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLO001 |  | CLOCK battery, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 4 |  |  | 4 |  |  |  |  | CHA063 |  | CHAIR, height adjustable, with arms, high back, swivel, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA083 |  | CHAIR, stacking, polypropylene, with back and seat pads | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM038 |  | COMPUTER PRINTER, laser, A4, 250H 380W 385D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | PRI017 |  | PRINTER bar code label, 230H 240W 370D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB179 |  | TABLE, 720H 900W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0904
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0904 |  |  |  |  | Laboratory: Cytopathology, cytology processing No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from specimen reception. 2) Preparing batched specimens, by centrifugation, processing of sputum (within protective cabinet). 3) Processing specimens/smear preparing and slide fixing. 4) Staining slides by mechanised machines or manually for routine or special techniques. 5) Staining of slide preparations. 6) Slide labelling and drying in oven. 7) Applying manually or mechanically a glass coverslip over the section with styrene mounted and labelling slides. 8) Holding of "in use" reagents, flammable solvents, laboratory media and small items of equipment. 9) Storage of samples/specimens under refrigerated/deep freeze conditions. 10) Disposal of liquid waste. 11) Displaying notices. 12) Holding of protective clothing for staff entering and leaving the laboratory area. 13) Clinical hand washing.
| Personnel: | [6 empty] | Up to 4 staff
| Planning Relationships: | [5 empty] | Easy access from laboratory specimen reception.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 63 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Telephone outlet with `hands off' facility. Deionised water should be provided using resin based filter or points of use.
| ADB | [7 empty] | Room Environmental Data
L0904
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0904 |  |  |  |  | Laboratory: Cytopathology, cytology processing No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG<BR>To Cytopathology Screening.
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 124
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 124 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0904
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0904 |  |  |  |  | Laboratory: Cytopathology, cytology processing No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0904
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0904 |  |  |  |  | Laboratory: Cytopathology, cytology processing No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | DRA008 |  | DRAINAGE, catchpot | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | EXT150 |  | EXTRACT, cabinet microbiological, exhaust protective class 1, BS5726 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | LWB090 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 3000W 750D, HTM67 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWS175 |  | WORKTOP, with sink on right (sink size 200x450x365), 920H 1500W 750D, HTM67 | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP022 |  | TAP, laboratory, cold water | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP060 |  | TAP laboratory water demineralised | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | WOR045 |  | LAB BENCH D/F STAINING W/TROUGH 2M | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAB072 |  | CABINET, exhaust protective, Class 1 microbiological safety BS5726, recirculating with integral fan and dual in line hepa filters,1420H 1200W 620D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | WAS051 |  | WASH, eye, first aid, with mirror, wall mounted, 360H 250W 100D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CEN023 |  | CENTRIFUGE, cytospin 4 with Starter kit, bench top, 240H 620W 405D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB076 |  | COVER SLIPPER AUTOMATIC | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB078 |  | MACHINE, slide drying, linear, 155H 1050W 155D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB101 |  | COUNTING CHAMBER SEMEN | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB106 |  | STAINING MACHINE for slides, 24 station, with heater and monitor, 600H 760 dia. | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB107 |  | STAINER SLIDE LINEAR AUTO, 300H 150W 1500D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0905
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0905 |  |  |  |  | Laboratory: Cytopathology, liquid based cytology processing No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from specimen reception. 2) Preparing batched specimens, by centrifugation, processing of sputum (within protective cabinet). 3) Processing specimens/smear preparing and slide fixing. 4) Staining slides by mechanised machines or manually for routine or special techniques. 5) Staining of slide preparations. 6) Slide labelling and drying in oven. 7) Applying manually or mechanically a glass coverslip over the section with styrene mounted and labelling slides. 8) Holding of "in use" reagents, flammable solvents, laboratory media and small items of equipment. 9) Storage of samples/specimens under refrigerated/deep freeze conditions. 10) Storing consumables: i.e. collection vials, preservatives and biohazard vessels. 11) Small items of equipment and sundries are stored. 12) Disposal of liquid waste. 13) Displaying notices. 14) Holding of protective clothing for staff entering and leaving the laboratory area. 15) Clinical hand washing.
| Personnel: | [6 empty] | Up to 4 staff
| Planning Relationships: | [5 empty] | Associated with Histopathology. Direct access to screening area. Easy access for rapid & convenient transfer of specimens from Histopathology specimen reception bench. Near to Histopathology Main laboratory. Convenient access from Consultant's, Junior Medical staff, Head MLSO's, & secretarial offices. Room - subdivided.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 63 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | LBC = Liquid-based cytopathology. Telephone outlet with `hands off' facility. Deionised water should be provided using resin based filter or points of use.
| ADB | [7 empty] | Room Environmental Data
L0905
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0905 |  |  |  |  | Laboratory: Cytopathology, liquid based cytology processing No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG<BR>To Cytopathology Screening.
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | A/B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 125
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 125 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0905
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0905 |  |  |  |  | Laboratory: Cytopathology, liquid based cytology processing No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0905
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0905 |  |  |  |  | Laboratory: Cytopathology, liquid based cytology processing No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | DRA008 |  | DRAINAGE, catchpot | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | EXT150 |  | EXTRACT, cabinet microbiological, exhaust protective class 1, BS5726 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWB090 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 3000W 750D, HTM67 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWS175 |  | WORKTOP, with sink on right (sink size 200x450x365), 920H 1500W 750D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP060 |  | TAP laboratory water demineralised | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | WOR045 |  | LAB BENCH D/F STAINING W/TROUGH 2M | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAB072 |  | CABINET, exhaust protective, Class 1 microbiological safety BS5726, recirculating with integral fan and dual in line hepa filters,1420H 1200W 620D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLO001 |  | CLOCK battery, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | WAS051 |  | WASH, eye, first aid, with mirror, wall mounted, 360H 250W 100D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CEN023 |  | CENTRIFUGE, cytospin 4 with Starter kit, bench top, 240H 620W 405D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB052 |  | MIXER, vortex | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB076 |  | COVER SLIPPER AUTOMATIC | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB078 |  | MACHINE, slide drying, linear, 155H 1050W 155D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB101 |  | COUNTING CHAMBER SEMEN | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB106 |  | STAINING MACHINE for slides, 24 station, with heater and monitor, 600H 760 dia. | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LAB107 |  | STAINER SLIDE LINEAR AUTO, 300H 150W 1500D | [16 empty] | 3
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0905
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0905 |  |  |  |  | Laboratory: Cytopathology, liquid based cytology processing No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | LAB191 |  | SEMI-AUTOMATIC LIQUID BASED CYTOLOGY SLIDE PREPARATION | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAB193 |  | AUTOMATIC LIQUID BASED CYTOLOGY SLIDE PREPARATION | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0907
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0907 |  |  |  |  | Reporting room: Cytopathology, 12 workstations No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reporting on cytopathology tests. 2) Computer workstation(s) may be used. 3) Printer may be used.
| Personnel: | [6 empty] | 12 x Staff
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 63 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
L0907
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0907 |  |  |  |  | Reporting room: Cytopathology, 12 workstations No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
Type Of Control:
Daytime General Service Illuminance (Lux):
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 126
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 126 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0907
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0907 |  |  |  |  | Reporting room: Cytopathology, 12 workstations No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Blinds are required. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0907
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0907 |  |  |  |  | Reporting room: Cytopathology, 12 workstations No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 12 |  |  | 12 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 12 |  |  | 12 |  |  |  |  | LWB055 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1500W 750D, HTM67 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 12 |  |  | 12 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 12 |  |  | 12 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 12 |  |  | 12 |  |  |  |  | SHE249 |  | SHELF, 2000W 300D | [16 empty] | 1
| 12 |  |  | 12 |  |  |  |  | SHE482 |  | SHELF, 2000W 200D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 12 |  |  | 12 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 12 |  |  | 12 |  |  |  |  | CHA063 |  | CHAIR, height adjustable, with arms, high back, swivel, 5 star base, on castors | [16 empty] | 3
| 12 |  |  | 12 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 12 |  |  | 12 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 12 |  |  | 12 |  |  |  |  | DES009 |  | DESK, cantilever, double pedestal 3 drawer and filing, cable management, modesty panel, 1600W 800D | [16 empty] | 3
| 12 |  |  | 12 |  |  |  |  | MIC025 |  | MICROSCOPE, binocular, 300H 200W 300D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0909
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0909 |  |  |  |  | Screening area: Cytopathology, 12 workstations No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Staining of slide preparations. 2) Carrying out examination of specimens using a microscope. 3) Reading and recording results and writing reports. 4) Displaying notices. 5) Holding of protective clothing for staff entering and leaving the laboratory area. 6) Clinical hand washing.
| Personnel: | [6 empty] | Up to 12 staff
| Planning Relationships: | [5 empty] | Direct access from Processing area. Convenient access from Consultant's, Junior Medical staff, Head MLSO's & secretarial offices.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 63 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
L0909
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0909 |  |  |  |  | Screening area: Cytopathology, 12 workstations No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | POS<BR>Cytopathogy.NEG to circulation
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
Type Of Control:
Daytime General Service Illuminance (Lux):
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 127
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 127 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0909
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0909 |  |  |  |  | Screening area: Cytopathology, 12 workstations No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Blinds are required. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0909
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0909 |  |  |  |  | Screening area: Cytopathology, 12 workstations No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 12 |  |  | 12 |  |  |  |  | LWB075 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 1500W 750D. | [16 empty] | 1
| 12 |  |  | 12 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 12 |  |  | 12 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO001 |  | CLOCK battery, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN021 |  | BIN/HOLDER clinical waste, small 77L CAP | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CAB052 |  | CABINET, slide storage, 14 drawer, capacity 6000 slides, 140H 480W 480D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | CAM020 |  | CAMERA DIGITAL for microscope, 500H 150W 150D | [16 empty] | 3
| 12 |  |  | 12 |  |  |  |  | CHA002 |  | CHAIR, height adjustable, medium back, swivel, 5 star base, on castors | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | COM029 |  | VDU DISPLAY for use with microscope, 450H 450W 150D | [16 empty] | 3
| 12 |  |  | 12 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 12 |  |  | 12 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 12 |  |  | 12 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM038 |  | COMPUTER PRINTER, laser, A4, 250H 380W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 12 |  |  | 12 |  |  |  |  | MIC025 |  | MICROSCOPE, binocular, 300H 200W 300D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | MIC030 |  | MICROSCOPE, dual head, 450H 500W 800D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L0910
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0910 |  |  |  |  | Store: Cytopathology, slide No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Storage of slides.
Personnel:
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
L0910
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0910 |  |  |  |  | Store: Cytopathology, slide No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
Type Of Control:
Daytime General Service Illuminance (Lux):
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 128
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 128 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L0910
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0910 |  |  |  |  | Store: Cytopathology, slide No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L0910
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L0910 |  |  |  |  | Store: Cytopathology, slide No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 20 |  |  | 20 |  |  |  |  | CAB052 |  | CABINET, slide storage, 14 drawer, capacity 6000 slides, 140H 480W 480D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1120
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1120 |  |  |  |  | Reception: departmental and specimen No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Specimens are received and logged. 2) Visual display terminal(s) may be used.
| Personnel: | [6 empty] | Up to 2 staff
| Planning Relationships: | [5 empty] | Adjacent to sorting area. Near to department main entrance.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 10.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Clock for recording receipt of specimens. Main Pneumatic Air Transport System - project team option. Facilities should be provided for the reception of specimens contaminated with radioactive materials or highly infectious specimens.
| ADB | [7 empty] | Room Environmental Data
L1120
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1120 |  |  |  |  | Reception: departmental and specimen No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 500 |  | Over desk task area
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 129
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 129 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1120
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1120 |  |  |  |  | Reception: departmental and specimen No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Essential Glazed sliding hatch, lockable Designation to be validated against current documentation
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1120
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1120 |  |  |  |  | Reception: departmental and specimen No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL028 |  | BELL, call, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HAT050 |  | HATCH, vertical sliding, glass, lockable, 1350H 1500W | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWB012 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1200W 600D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO004 |  | CLOCK battery with second sweep hand, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CHA003 |  | CHAIR, height adjustable 540-790, tilting back, adjustable footrest, swivel, 5 star base, on glides | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CUP378 |  | CUPBOARD/DRAWER UNIT, 1 drawer, 1 shelf, on castors, 660H 480W 390D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1126
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1126 |  |  |  |  | Central wash-up Pathology No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Disinfection of contaminated material, equipment, plastic media containers and glassware prior to cleaning or disposal. 2) Labelling items for autoclaving. 3) Disposal of liquid waste. 4) Disposal of solid waste. 5) Machine washing glassware. 6) Hand washing glassware. 7) Sterilizing bulk media. 8) Drying glassware. 9) Holding bagged, possibly contaminated material, for disposal. 10) Preparation of distilled water. 11) Emergency eye irrigation following contamination with corrosive or irritant substances. 12) Clinical hand washing.
| Personnel: | [6 empty] | 1 -2 staff
| Planning Relationships: | [5 empty] | Direct access to Media preparation room. Easy access for maintenance of autoclaving equipment.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
L1126
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1126 |  |  |  |  | Central wash-up Pathology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | NEG
| Supply Air: Final Filter Class | [12 empty] | F7
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 160.948081264108
Daytime Specific Service Illuminance (Lux):
| Nighttime General Service Illuminance (Lux): | [13 empty] | 22.8947368421052
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 82.5498060031674
| Unified Glare Rating Limit (UGRL): | [13 empty] | 18.5296442687747
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 130
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 130 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1126
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1126 |  |  |  |  | Central wash-up Pathology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1126
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1126 |  |  |  |  | Central wash-up Pathology No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DSU013 |  | DISPOSAL UNIT, hopper with flushing rim, 110mm outlet, no tap holes no overflow, back inlet, stainless steel, 900H 600W 600D. | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT067 |  | OUTLET isolator 15amp, TP&N | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT301 |  | OUTLET, cold water for equipment | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT342 |  | OUTLET, drain point | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP001 |  | TAP extension piece(bib/pillar), length to suit | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | TAP343 |  | *TAP pillar 12mm, high neck. HTM64TP3. Replaced by: TAP359, 15/05/06 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | TAP345 |  | *TAP pillar 12mm, high neck, drinking, HTM64TP3. Replaced by: TAP359, 15/05/06 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WKT152 |  | WORKTOP, cantilevered from wall, 2400W 650D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WKT520 |  | WORKTOP, plain, stainless steel, with 2 sink bowls & drainers, cantilevered from wall, 2400W 650D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOT001 |  | BOTTLE, eye irrigation, emergency, with internal application, fix panel | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB110 |  | STILL, distilled water, 8l/hr, wall mounted, 410H 550W 240D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB113 |  | WASHING MACHINE, laboratory glassware, 900H 700W 820D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | RAC010 |  | RACK, draining equipment, wall mounted, 450H 300W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB019 |  | CABINET, drying, glassware, 1625H 1170W 610D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC425 |  | RACK, metal, 2 bays, 4 shelves, 1980H 1800W 450D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO010 |  | TROLLEY, autoclave, 950H 1150W 700D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO269 |  | TROLLEY, waste disposal, fibreglass, 570H 550W 550D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1130
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1130 |  |  |  |  | Sorting and request processing area: specimen No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Sorting, batching and labelling/numbering specimens and processing request forms. 2) Visual display terminal(s) may be used.
| Personnel: | [6 empty] | 1 - 2 staff
| Planning Relationships: | [5 empty] | Adjacent to reception area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 10.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Barcode reader/scanner with charging unit are require.
| ADB | [7 empty] | Room Environmental Data
L1130
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1130 |  |  |  |  | Sorting and request processing area: specimen No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -Ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN15. Formalin extract may be required. Safe handling for radioactive or infectious samples may be required.
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1130
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1130 |  |  |  |  | Sorting and request processing area: specimen No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1130
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1130 |  |  |  |  | Sorting and request processing area: specimen No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLO001 |  | CLOCK battery, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CAB025 |  | CABINET, filing, 4 drawer, 1320H 465W 620D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA063 |  | CHAIR, height adjustable, with arms, high back, swivel, 5 star base, on castors | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA083 |  | CHAIR, stacking, polypropylene, with back and seat pads | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM038 |  | COMPUTER PRINTER, laser, A4, 250H 380W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP011 |  | CUPBOARD, metal, with 4 pull out galvanised shelves, lockable, 1800H 1000W 500D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | DES022 |  | DESK, cantilever, single pedestal 3 drawer, cable management, modesty panel, 1600W 800D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | DES027 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1600W 800D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DES028 |  | DESK RETURN UNIT, cantilever, cable management, adjustable legs, modesty panel, freestanding, 1200W 600D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | PRI017 |  | PRINTER bar code label, 230H 240W 370D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB179 |  | TABLE, 720H 900W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1131 |  |  |  |  | Sorting and request processing area: specimen No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Sorting, batching and labelling/numbering specimens and processing request forms. 2) Visual display terminal(s) may be used.
| Personnel: | [6 empty] | Up to 3 staff
| Planning Relationships: | [5 empty] | Adjacent to reception area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Barcode reader/scanner with charging unit are require.
| ADB | [7 empty] | Room Environmental Data
L1131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1131 |  |  |  |  | Sorting and request processing area: specimen No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -Ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN15. Formalin extract may be required. Safe handling for radioactive or infectious samples may be required.
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1131 |  |  |  |  | Sorting and request processing area: specimen No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1131
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1131 |  |  |  |  | Sorting and request processing area: specimen No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 4 |  |  | 4 |  |  |  |  | HOO024 |  | HOOK, hat and coat, 1 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWB060 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 2000W 750D, HTM67 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWB080 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 2000W 750D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLO001 |  | CLOCK battery, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS026 |  | DISPENSER, Medical hand sanitizer, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 4 |  |  | 4 |  |  |  |  | CAB025 |  | CABINET, filing, 4 drawer, 1320H 465W 620D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | CHA063 |  | CHAIR, height adjustable, with arms, high back, swivel, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA083 |  | CHAIR, stacking, polypropylene, with back and seat pads | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM038 |  | COMPUTER PRINTER, laser, A4, 250H 380W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CUP011 |  | CUPBOARD, metal, with 4 pull out galvanised shelves, lockable, 1800H 1000W 500D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | DES027 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1600W 800D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | DES028 |  | DESK RETURN UNIT, cantilever, cable management, adjustable legs, modesty panel, freestanding, 1200W 600D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | PRI017 |  | PRINTER bar code label, 230H 240W 370D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TAB179 |  | TABLE, 720H 900W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO181 |  | TROLLEY, general purpose, 3 tier, buffered, 950H 890W 590D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1136
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1136 |  |  |  |  | Processing area: specimen No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from specimen reception. 2) Holding specimens prior to delivery to other laboratories. 3) Provision of refrigerated storage. 4) Small items of equipment and sundries are stored. 5) Dealing with specimens which have arrived in leaking or otherwise damaged containers. 6) Clinical waste may be disposed 7) Hanging protective clothing. 8) Clinical hand washing.
| Personnel: | [6 empty] | 1 -2 Staff
| Planning Relationships: | [5 empty] | Directly connected to the laboratories receiving samples (for example via a hole in the wall).
| Space Data: | [6 empty] | Area (m²): |  |  |  | 10.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Facilities should be provided for the reception of specimens contaminated with radioactive materials or highly infectious specimens. Area should be provided for centrifuging, aliquoting, and dispatching. Facilities should also be provided for decontamination of staff.
| ADB | [7 empty] | Room Environmental Data
L1136
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1136 |  |  |  |  | Processing area: specimen No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -Ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN15. Formalin extract may be required. Safe handling for radioactive or infectious samples may be required.
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1136
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1136 |  |  |  |  | Processing area: specimen No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1136
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1136 |  |  |  |  | Processing area: specimen No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWB015 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1500W 600D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWS055 |  | WORKTOP, with sink on right (sink size 200x450x365), 720H 1500W 750D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB072 |  | CABINET, exhaust protective, Class 1 microbiological safety BS5726, recirculating with integral fan and dual in line hepa filters,1420H 1200W 620D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CEN016 |  | CENTRIFUGE, refrigerated, floor standing, 1140H 760W 990D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | WAS051 |  | WASH, eye, first aid, with mirror, wall mounted, 360H 250W 100D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CEN004 |  | CENTRIFUGE, bench, includes: swingout, various fixed angle and microplate rotors and inserts, 300H 300W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL004 |  | HOLDER, sack, with lid foot operated, small, freestanding | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LST059 |  | BIN UNIT, underbench, mobile, 650H 350W 500D, HTM67 | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF066 |  | REFRIGERATOR, capacity 390 litres, 1855H 645W 595D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF120 |  | REFRIGERATOR/FREEZER, capacity 160 litre refrigerator, 126 litre freezer, 1650H 550W 610D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | STO023 |  | STOOL, laboratory, complete with footring | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1137
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1137 |  |  |  |  | Processing area: specimen No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from specimen reception. 2) Holding specimens prior to delivery to other laboratories. 3) Provision of refrigerated storage. 4) Small items of equipment and sundries are stored. 5) Dealing with specimens which have arrived in leaking or otherwise damaged containers. 6) Clinical waste may be disposed 7) Hanging protective clothing. 8) Clinical hand washing.
| Personnel: | [6 empty] | Up to 3 staff
| Planning Relationships: | [5 empty] | Directly connected to the laboratories receiving samples (for example via a hole in the wall).
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Facilities should be provided for the reception of specimens contaminated with radioactive materials or highly infectious specimens. Area should be provided for centrifuging, aliquoting, and dispatching. Facilities should also be provided for decontamination of staff.
| ADB | [7 empty] | Room Environmental Data
L1137
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1137 |  |  |  |  | Processing area: specimen No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -Ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN15. Formalin extract may be required. Safe handling for radioactive or infectious samples may be required.
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1137
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1137 |  |  |  |  | Processing area: specimen No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1137
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1137 |  |  |  |  | Processing area: specimen No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | LWB015 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1500W 600D, HTM67 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWS055 |  | WORKTOP, with sink on right (sink size 200x450x365), 720H 1500W 750D, HTM67 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB072 |  | CABINET, exhaust protective, Class 1 microbiological safety BS5726, recirculating with integral fan and dual in line hepa filters,1420H 1200W 620D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CEN016 |  | CENTRIFUGE, refrigerated, floor standing, 1140H 760W 990D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | WAS051 |  | WASH, eye, first aid, with mirror, wall mounted, 360H 250W 100D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CEN004 |  | CENTRIFUGE, bench, includes: swingout, various fixed angle and microplate rotors and inserts, 300H 300W 300D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL004 |  | HOLDER, sack, with lid foot operated, small, freestanding | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LST059 |  | BIN UNIT, underbench, mobile, 650H 350W 500D, HTM67 | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF066 |  | REFRIGERATOR, capacity 390 litres, 1855H 645W 595D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF120 |  | REFRIGERATOR/FREEZER, capacity 160 litre refrigerator, 126 litre freezer, 1650H 550W 610D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | STO023 |  | STOOL, laboratory, complete with footring | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1138
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1138 |  |  |  |  | Processing area: specimen No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Reception of specimens from specimen reception. 2) Holding specimens prior to delivery to other laboratories. 3) Provision of refrigerated storage. 4) Small items of equipment and sundries are stored. 5) Dealing with specimens which have arrived in leaking or otherwise damaged containers. 6) Clinical waste may be disposed 7) Hanging protective clothing. 8) Clinical hand washing.
| Personnel: | [6 empty] | Up to 4 staff
| Planning Relationships: | [5 empty] | Directly connected to the laboratories receiving the sample.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Facilities should be provided for the reception of specimens contaminated with radioactive materials or highly infectious specimens. Area should be provided for centrifuging, aliquoting, and dispatching. Facilities should also be provided for decontamination of staff.
| ADB | [7 empty] | Room Environmental Data
L1138
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1138 |  |  |  |  | Processing area: specimen No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -Ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN15. Formalin extract may be required. Safe handling for radioactive or infectious samples may be required.
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1138
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1138 |  |  |  |  | Processing area: specimen No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar control. Security device Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1138
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1138 |  |  |  |  | Processing area: specimen No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO018 |  | HOOK, coat, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | LWB015 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1500W 600D, HTM67 | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | LWS055 |  | WORKTOP, with sink on right (sink size 200x450x365), 720H 1500W 750D, HTM67 | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 12 |  |  | 12 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CAB072 |  | CABINET, exhaust protective, Class 1 microbiological safety BS5726, recirculating with integral fan and dual in line hepa filters,1420H 1200W 620D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CEN016 |  | CENTRIFUGE, refrigerated, floor standing, 1140H 760W 990D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | WAS051 |  | WASH, eye, first aid, with mirror, wall mounted, 360H 250W 100D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | CEN004 |  | CENTRIFUGE, bench, includes: swingout, various fixed angle and microplate rotors and inserts, 300H 300W 300D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM031 |  | COMPUTER CPU | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM032 |  | COMPUTER VDT MONITOR | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM035 |  | COMPUTER PRINTER, line, small | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL004 |  | HOLDER, sack, with lid foot operated, small, freestanding | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | LST059 |  | BIN UNIT, underbench, mobile, 650H 350W 500D, HTM67 | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF066 |  | REFRIGERATOR, capacity 390 litres, 1855H 645W 595D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | REF120 |  | REFRIGERATOR/FREEZER, capacity 160 litre refrigerator, 126 litre freezer, 1650H 550W 610D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STO023 |  | STOOL, laboratory, complete with footring | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1140
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1140 |  |  |  |  | Common equipment room Laboratory No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Small items of equipment and sundries are stored. 2) Miscellaneous equipment is stored. 3) Large items of equipment are stored.
| Personnel: | [6 empty] | 1 x Staff Intermittent use
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Equipment stored is project specific.
| ADB | [7 empty] | Room Environmental Data
L1140
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1140 |  |  |  |  | Common equipment room Laboratory No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -Ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN15. Formalin extract may be required. Safe handling for radioactive or infectious samples may be required.
LIGHTING
| Type Of Control: | [13 empty] | N/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1140
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1140 |  |  |  |  | Common equipment room Laboratory No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Not applicable or obscured glass Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1140
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1140 |  |  |  |  | Common equipment room Laboratory No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1142
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1142 |  |  |  |  | Refrigerator/freezer room Pathology No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Storage of samples/specimens under refrigerated/deep freeze conditions.
| Personnel: | [6 empty] | 1 x Staff
| Planning Relationships: | [5 empty] | Easy access to areas served.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Externally mounted temperature recorder (sensors inside), readily visible, easy accessible. Continuously maintained alarm panel, local/remote control of high/low temp.
| ADB | [7 empty] | Room Environmental Data
L1142
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1142 |  |  |  |  | Refrigerator/freezer room Pathology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -Ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN15
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1142
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1142 |  |  |  |  | Refrigerator/freezer room Pathology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Specialist door, emergency opening release from within space.
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1142
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1142 |  |  |  |  | Refrigerator/freezer room Pathology No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | ALA015 |  | ALARM UNIT audible, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWB032 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 1200W 600D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LAB007 |  | FREEZER, -70 deg.C, floor standing, 1650H 1025W 1210D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | REF103 |  | REFRIGERATED DEEP FREEZE, capacity 327 litres, vertical type, sparkfree interior, 1840H 660W 685D | [16 empty] | 2
| 4 |  |  | 4 |  |  |  |  | RAC379 |  | RACK, stainless steel, 4 wire shelves shelves, 1590H 1220W 455D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | REF060 |  | REFRIGERATOR, reagents, capacity 110 litre, external temperature gauge, automatic defrost, underbench, 850H 500W 590D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1143
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1143 |  |  |  |  | Refrigerator/freezer room Pathology No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Storage of samples/specimens under refrigerated/deep freeze conditions.
| Personnel: | [6 empty] | 1 - 2 Staff
| Planning Relationships: | [5 empty] | Easy access to areas served.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Externally mounted temperature recorder (sensors inside), readily visible, easy accessible. Continuously maintained alarm panel, local/remote control of high/low temp.
| ADB | [7 empty] | Room Environmental Data
L1143
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1143 |  |  |  |  | Refrigerator/freezer room Pathology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -Ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN15
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1143
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1143 |  |  |  |  | Refrigerator/freezer room Pathology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Specialist door, emergency opening release from within space.
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1143
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1143 |  |  |  |  | Refrigerator/freezer room Pathology No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | ALA015 |  | ALARM UNIT audible, wall mounted | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWB032 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 1200W 600D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 5 |  |  | 5 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LAB007 |  | FREEZER, -70 deg.C, floor standing, 1650H 1025W 1210D | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | REF103 |  | REFRIGERATED DEEP FREEZE, capacity 327 litres, vertical type, sparkfree interior, 1840H 660W 685D | [16 empty] | 2
| 4 |  |  | 4 |  |  |  |  | RAC379 |  | RACK, stainless steel, 4 wire shelves shelves, 1590H 1220W 455D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | REF060 |  | REFRIGERATOR, reagents, capacity 110 litre, external temperature gauge, automatic defrost, underbench, 850H 500W 590D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1145
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1145 |  |  |  |  | Cold room: 4 deg C Pathology No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Storing at 4 DegC specimens and reagents.
| Personnel: | [6 empty] | 1 x Staff
| Planning Relationships: | [5 empty] | Easy access to areas served.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Externally mounted temperature recorder (sensors inside), readily visible, easy accessible. Continuously maintained alarm panel, local/remote control of high/low temp.
| ADB | [7 empty] | Room Environmental Data
L1145
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1145 |  |  |  |  | Cold room: 4 deg C Pathology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 4
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | n/a
| Minimum Air Changes (AC/hr): | [13 empty] | -
| Ventilation Type: | [13 empty] | -
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | -
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN15
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Air Sampling System to be considered
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1145
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1145 |  |  |  |  | Cold room: 4 deg C Pathology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Specialist door, emergency opening release from within space.
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1145
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1145 |  |  |  |  | Cold room: 4 deg C Pathology No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | ALA015 |  | ALARM UNIT audible, wall mounted | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWB012 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1200W 600D, HTM67 | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | SHE221 |  | SHELF, 1200W 300D | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | RAC379 |  | RACK, stainless steel, 4 wire shelves shelves, 1590H 1220W 455D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1147
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1147 |  |  |  |  | Cryopreservation room Laboratory No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Storage of specimens in liquid nitrogen. 2) Storing face shields cryogenic gloves and aprons.
Personnel:
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Space required to accommodate liquid nitrogen freezers, which come in a range of sizes.
| ADB | [7 empty] | Room Environmental Data
L1147
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1147 |  |  |  |  | Cryopreservation room Laboratory No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -Ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN15. Continuous ventilation required with boost in event of spillage.
LIGHTING
Type Of Control:
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | N
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Air Sampling System to be considered
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1147
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1147 |  |  |  |  | Cryopreservation room Laboratory No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Doorsets:
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1147
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1147 |  |  |  |  | Cryopreservation room Laboratory No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1148
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1148 |  |  |  |  | Cryopreservation room Laboratory No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Storage of specimens in liquid nitrogen. 2) Storing face shields cryogenic gloves and aprons.
Personnel:
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Space required to accommodate liquid nitrogen freezers, which come in a range of sizes.
| ADB | [7 empty] | Room Environmental Data
L1148
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1148 |  |  |  |  | Cryopreservation room Laboratory No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -Ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN15. Continuous ventilation required with boost in event of spillage.
LIGHTING
Type Of Control:
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | N
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | Air Sampling System to be considered
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1148
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1148 |  |  |  |  | Cryopreservation room Laboratory No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Doorsets:
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1148
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1148 |  |  |  |  | Cryopreservation room Laboratory No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1151
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1151 |  |  |  |  | Hot room: 37 DegC Microbiology No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Incubation of inoculated material, liquid and contaminated media in tubes or plates at +37 DegC.
| Personnel: | [6 empty] | 1 - 2 Staff
| Planning Relationships: | [5 empty] | Close to areas served.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Externally mounted temperature recorder (sensors inside), readily visible, easy accessible. Continuously maintained alarm panel, local/remote control of high/low temp.
| ADB | [7 empty] | Room Environmental Data
L1151
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1151 |  |  |  |  | Hot room: 37 DegC Microbiology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 37
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | n/a
| Minimum Air Changes (AC/hr): | [13 empty] | -
| Ventilation Type: | [13 empty] | -
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | -
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN15
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1151
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1151 |  |  |  |  | Hot room: 37 DegC Microbiology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Specialist door, emergency opening release from within space.
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1151
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1151 |  |  |  |  | Hot room: 37 DegC Microbiology No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | LWS175 |  | WORKTOP, with sink on right (sink size 200x450x365), 920H 1500W 750D, HTM67 | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | SHE231 |  | SHELF, 1500W 300D | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | LAB022 |  | SHAKING MACHINE, orbital, 125H 320W 375D | [16 empty] | 3
| 4 |  |  | 4 |  |  |  |  | RAC379 |  | RACK, stainless steel, 4 wire shelves shelves, 1590H 1220W 455D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1152
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1152 |  |  |  |  | Hot room: 37 DegC Microbiology No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Incubation of inoculated material, liquid and contaminated media in tubes or plates at +37 DegC.
| Personnel: | [6 empty] | 3 Staff
| Planning Relationships: | [5 empty] | Close to areas served.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Externally mounted temperature recorder (sensors inside), readily visible, easy accessible. Continuously maintained alarm panel, local/remote control of high/low temp.
| ADB | [7 empty] | Room Environmental Data
L1152
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1152 |  |  |  |  | Hot room: 37 DegC Microbiology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 37
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | n/a
| Minimum Air Changes (AC/hr): | [13 empty] | -
| Ventilation Type: | [13 empty] | -
| Pressure Relative to Adjoining Space: | [13 empty] | Bal
| Supply Air: Final Filter Class | [12 empty] | -
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN15
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1152
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1152 |  |  |  |  | Hot room: 37 DegC Microbiology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Specialist door, emergency opening release from within space.
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1152
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1152 |  |  |  |  | Hot room: 37 DegC Microbiology No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | LWS175 |  | WORKTOP, with sink on right (sink size 200x450x365), 920H 1500W 750D, HTM67 | [16 empty] | 1
| 10 |  |  | 10 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 10 |  |  | 10 |  |  |  |  | SHE231 |  | SHELF, 1500W 300D | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | LAB022 |  | SHAKING MACHINE, orbital, 125H 320W 375D | [16 empty] | 3
| 5 |  |  | 5 |  |  |  |  | RAC379 |  | RACK, stainless steel, 4 wire shelves shelves, 1590H 1220W 455D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1153
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1153 |  |  |  |  | Darkroom No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Visualising DNA under UV light.
| Personnel: | [6 empty] | 1 -3 staff Intermittent
| Planning Relationships: | [5 empty] | Close to electrophoresis.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 10.5 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
L1153
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1153 |  |  |  |  | Darkroom No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -Ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN15
LIGHTING
| Type Of Control: | [13 empty] | Sp/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 50-300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1153
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1153 |  |  |  |  | Darkroom No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - lightproof, outside release: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1153
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1153 |  |  |  |  | Darkroom No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | LWB012 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1200W 600D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LWS055 |  | WORKTOP, with sink on right (sink size 200x450x365), 720H 1500W 750D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1154
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1154 |  |  |  |  | Darkroom Microbiology No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Visualising DNA under UV light.
| Personnel: | [6 empty] | 1 -3 staff Intermittent
| Planning Relationships: | [5 empty] | Close to electrophoresis.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 31.5 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
L1154
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1154 |  |  |  |  | Darkroom Microbiology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -Ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN15
LIGHTING
| Type Of Control: | [13 empty] | Sp/S
| Daytime General Service Illuminance (Lux): | [13 empty] | 50-300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to SLL Lighting Guide 2 for more detailed guidance
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1154
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1154 |  |  |  |  | Darkroom Microbiology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - lightproof, outside release: 1 x personnel & equipment access (1000mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1154
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1154 |  |  |  |  | Darkroom Microbiology No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 3 |  |  | 3 |  |  |  |  | LWB015 |  | WORKBENCH laboratory, C-frame, freestanding, 720H 1500W 600D, HTM67 | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LWS055 |  | WORKTOP, with sink on right (sink size 200x450x365), 720H 1500W 750D, HTM67 | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1156
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1156 |  |  |  |  | Centrifuge room Laboratory No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Centrifuging.
| Personnel: | [6 empty] | Up to 3 staff.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
Notes:
| ADB | [7 empty] | Room Environmental Data
L1156
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1156 |  |  |  |  | Centrifuge room Laboratory No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -Ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN15
LIGHTING
| Type Of Control: | [13 empty] | S/V
| Daytime General Service Illuminance (Lux): | [13 empty] | 500
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive, not including Centrifuge unit.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1156
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1156 |  |  |  |  | Centrifuge room Laboratory No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control, security control as necessary, see BS2881 Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1156
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1156 |  |  |  |  | Centrifuge room Laboratory No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 3 |  |  | 3 |  |  |  |  | LWB075 |  | WORKBENCH laboratory, C-frame, freestanding, 920H 1500W 750D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | SHE249 |  | SHELF, 2000W 300D | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | CEN003 |  | CENTRIFUGE bench mounted, 300H 420W 490D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CEN012 |  | CENTRIFUGE, floor standing, mobile, 700H 670W 720D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CEN021 |  | CENTRIFUGE micro, high speed, 250H 305W340D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1162
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1162 |  |  |  |  | Sterilizer loading/unloading area: 2 autoclaves/sterilizers Pathology No room layout
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Receiving packaged products before sterilization. 2) Sterilizer is loaded/unloaded. 3) Sterilizing bulk media. 4) Drying glassware. 5) Processes and tests are recorded. 6) Storing records and test charts. 7) Labelling sterilized items. 8) Segregate and hold (a) items visibly defective following sterilization, (b) contents failed process cycle. 9) Storing sterile equipment. 10) Storing glassware.
| Personnel: | [6 empty] | Up to 3 staff
| Planning Relationships: | [5 empty] | Direct access from central wash-up area. Easy access to autoclave/sterilizer plant room.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Space will be required for: 1) Parking of empty autoclave trolleys & baskets. 2) Holding of material to be autoclaved i.e. loaded trolleys & baskets.
| ADB | [7 empty] | Room Environmental Data
L1162
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1162 |  |  |  |  | Sterilizer loading/unloading area: 2 autoclaves/sterilizers Pathology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18-25
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | -Ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
| General Notes: | [5 empty] | Refer to HBN15
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
| Local Task Illuminance (Lux): | [13 empty] | 500
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
| Standby Lighting Grade - Local Lighting: | [13 empty] | A
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1162
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1162 |  |  |  |  | Sterilizer loading/unloading area: 2 autoclaves/sterilizers Pathology No room layout
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset(s) subject to room layout: _ x personnel, trolley & equipment access (____mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control, security control as necessary, see BS2881 Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1162
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1162 |  |  |  |  | Sterilizer loading/unloading area: 2 autoclaves/sterilizers Pathology No room layout
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CLO005 |  | CLOCK impulse, wall mounted | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | LAB109 |  | AUTOCLAVE, 425 litres, multi-functional | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT067 |  | OUTLET isolator 15amp, TP&N | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT121 |  | SOCKET outlet, computer data, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT215 |  | SOCKET outlet, telephone | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE241 |  | SHELF, 1800W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WKT148 |  | WORKTOP, cantilevered from wall, 1800W 650D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | LAB112 |  | STERILIZER, glassware, hot air, 150 litres, floor standing | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB019 |  | CABINET, drying, glassware, 1625H 1170W 610D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC425 |  | RACK, metal, 2 bays, 4 shelves, 1980H 1800W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | STO003 |  | STOOL, height adjustable, on slides, 600-750H 320 dia. | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO010 |  | TROLLEY, autoclave, 950H 1150W 700D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO205 |  | TROLLEY, stainless steel, 1 shelf, 900H 600W 600D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | TRO269 |  | TROLLEY, waste disposal, fibreglass, 570H 550W 550D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1804
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1804 |  |  |  |  | Service room: clinical equipment: 2 places
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Electronic and Medical Engineering (EME) equipment may be serviced or repaired. 2) Minor scheduled/unscheduled servicing of equipment may be undeertaken by a visiting EME technician when full facilities of EME workshop are not required. 3) User servicing and instruction manuals for EME equipment are stored. 4) Computer workstation(s) may be used. 5) Telephone(s) may be used. 6) Piped medical gases, vacuum and associated equipment may be used. 7) Secure storage. 8) Clinical hand washing.
| Personnel: | [6 empty] | Up to 3 x staff. Intermittent use
| Planning Relationships: | [5 empty] | Good vision of the interior of this room is essential for the safety of the servicing personnel. Direct access from Dirty Utility. Direct access to Clinical equipment Store.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 21 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
L1804
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1804 |  |  |  |  | Service room: clinical equipment: 2 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 500 |  | Bench
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | non-ionising if radiation present
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1804
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1804 |  |  |  |  | Service room: clinical equipment: 2 places
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 3 sets of doors: 1 x personnel, wheelchair & equipment access (1000mm); 2 x personnel, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1804
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1804 |  |  |  |  | Service room: clinical equipment: 2 places
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 16 |  |  | 16 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT454 |  | OUTLET, 7 kPa compressed air, surgical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT461 |  | OUTLET, nitrous oxide, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT480 |  | OUTLET, gas scavenging (AGS), medical | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE201 |  | SHELF, 600W 300D | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | SHE211 |  | SHELF, 900W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SMW090 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 3000W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SWC062 |  | EMERGENCY STOP switch button, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | L1804-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1804-01 |  |  |  |  | Service room: clinical equipment
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Electronic and Medical Engineering (EME) equipment may be serviced or repaired. 2) Minor scheduled/unscheduled servicing of equipment may be undeertaken by a visiting EME technician when full facilities of EME workshop are not required. 3) User servicing and instruction manuals for EME equipment are stored. 4) Computer workstation(s) may be used. 5) Telephone(s) may be used. 6) Piped medical gases, vacuum and associated equipment may be used. 7) Secure storage. 8) Clinical hand washing.
| Personnel: | [6 empty] | Up to 2 x staff. Intermittent use
| Planning Relationships: | [5 empty] | Good vision of the interior of this room is essential for the safety of the servicing personnel. Direct access from Dirty Utility. Direct access to Clinical equipment Store.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
L1804-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1804-01 |  |  |  |  | Service room: clinical equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
| Daytime Specific Service Illuminance (Lux): | [13 empty] | 500 |  | Bench
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | High
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 43
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
| General Notes: | [5 empty] | Dedicated hot and cold water systems required to prevent cross contamination.
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | non-ionising if radiation present
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | L1804-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1804-01 |  |  |  |  | Service room: clinical equipment
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 3 sets of doors: 1 x personnel, wheelchair & equipment access (1000mm); 2 x personnel, trolley, wheelchair & equipment access (1500mm)
| Windows: | [5 empty] | Non-essential - Project Option Clear glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | L1804-01
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | L1804-01 |  |  |  |  | Service room: clinical equipment
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS101 |  | BASIN, medium, hospital pattern, vitreous china, no tap holes, no overflow, integral back outlet, 500W 400D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLO003 |  | CLOCK synchronous with second sweep hand, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 8 |  |  | 8 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT046 |  | CONNECTION UNIT, unswitched, 13 amp, flex outlet | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT453 |  | OUTLET, 4 kPa compressed air, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT454 |  | OUTLET, 7 kPa compressed air, surgical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT461 |  | OUTLET, nitrous oxide, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT470 |  | OUTLET, oxygen, medical. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT475 |  | OUTLET, vacuum, medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT480 |  | OUTLET, gas scavenging (AGS), medical | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE201 |  | SHELF, 600W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE211 |  | SHELF, 900W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMC013 |  | CABINET, base, modular storage, for 400 facing inserts, with door, on plinth, 900H | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SMW090 |  | WORKTOP, clinical, for 400 facing modular storage cabinets, 3000W 700D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC062 |  | EMERGENCY STOP switch button, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP892 |  | TAP, bib, 2x8 mm thermostatic mixer, automatic action, sensor operated, non-touch, | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS011 |  | DISPENSER, barrier cream, disposable single cartridge, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS438 |  | DISPENSER, disposable gloves set of 3 and disposable apron, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Clinical administration. 2) Computer workstation(s) may be used. 3) Telephone(s) may be used. 4) Discussions and interviews may take place. 5) Files and records are stored. 6) Hanging outdoor clothing. 7) Secure holding/storing of clothing and personal belongings. 8) Printer may be used. 9) Electronic patient records (EPRs) may be accessed and updated. 10) Staff notices, information and/or messages may be displayed. 11) Dealing with enquiries. 12) Information on computers may be accessed.
| Personnel: | [6 empty] | 1 x staff Up to x 2 others.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following equipment is shown on the room layout but is optional: - call repeat lamps for controlled drugs cupboards (but required if the office is used for clinical control). The following items may provided; - shelving; - printer. The following items may be provided if the office is used for clinical control: - a small safe; - a key cupboard; - an alarm panel, see HTM 08-03; - a dimming switch - recommended if the room is used for viewing digital images. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0251
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0251 |  |  |  |  | Office: 1 person
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 3 |  |  | 3 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG138 |  | LUMINAIRE, indicating controlled drugs cupboard repeat | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB049 |  | CABINET, lateral filing, 6 rails, 2 door, 1970H 1000W 470D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DES026 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1400W 700D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | DRA057 |  | DRAWER UNIT, 3 drawer, lockable, on castors, desk height 715H 430W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0252
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0252 |  |  |  |  | Office: 2 person
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Clinical administration. 2) Computer workstation(s) may be used. 3) Telephone(s) may be used. 4) Discussions and interviews may take place. 5) Files and records are stored. 6) Hanging outdoor clothing. 7) Staff notices, information and/or messages may be displayed. 8) Printer may be used. 9) Dealing with enquiries. 10) Information on computers may be accessed.
| Personnel: | [6 empty] | 2 x staff. Up to 2 x others.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following equipment is shown on the room layout but is optional: - call repeat lamps for controlled drugs cupboards (but required if the office is used for clinical control). The following items may be provided if the office is used for clinical control: - a dimming switch - recommended if the room is used for viewing digital images. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0252
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0252 |  |  |  |  | Office: 2 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0252
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0252 |  |  |  |  | Office: 2 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0252
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0252 |  |  |  |  | Office: 2 person
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 3 |  |  | 3 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG138 |  | LUMINAIRE, indicating controlled drugs cupboard repeat | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB049 |  | CABINET, lateral filing, 6 rails, 2 door, 1970H 1000W 470D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | DES026 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1400W 700D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | DRA057 |  | DRAWER UNIT, 3 drawer, lockable, on castors, desk height 715H 430W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0252-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0252-02 |  |  |  |  | Office: 3 person
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Clinical administration. 2) Computer workstation(s) may be used. 3) Telephone(s) may be used. 4) Discussions and interviews may take place. 5) Files and records are stored. 6) Hanging outdoor clothing. 7) Secure holding/storing of clothing and personal belongings.
| Personnel: | [6 empty] | 3 x staff. Up to 3 x others.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 18 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following equipment is shown on the room layout but is optional: - call repeat lamps for controlled drugs cupboards (but required if the office is used for clinical control). The following items may be provided if the office is used for clinical control: - a dimming switch - recommended if the room is used for viewing digital images. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0252-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0252-02 |  |  |  |  | Office: 3 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 40
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0252-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0252-02 |  |  |  |  | Office: 3 person
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0252-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0252-02 |  |  |  |  | Office: 3 person
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 5 |  |  | 5 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG138 |  | LUMINAIRE, indicating controlled drugs cupboard repeat | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CAB049 |  | CABINET, lateral filing, 6 rails, 2 door, 1970H 1000W 470D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | DES026 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1400W 700D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | DRA057 |  | DRAWER UNIT, 3 drawer, lockable, on castors, desk height 715H 430W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0268-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0268-02 |  |  |  |  | Administration area: continuous use: 6 workstations
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Clinical administration. 2) Computer workstation(s) may be used. 3) Telephone(s) may be used. 4) Files and records are stored. 5) Secure holding/storing of clothing and personal belongings. 6) Hanging outdoor clothing. 7) Printer may be used. 8) Electronic patient records (EPRs) may be accessed and updated. 9) Staff notices, information and/or messages may be displayed. 10) Dealing with enquiries. 11) Patient records may be reviewed and recorded. 12) Information on computers may be accessed. 13) Shredding documents.
| Personnel: | [6 empty] | 6 x staff. Up to 3 x others.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 30 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The layout illustrates socket outlets at desk height because they should be easily accessible to enable equipment to be switched off for energy conservation. Floor box services are discouraged as they make it harder to convert the space into a clinical room in the future. It is therefore assumed that the workstations are wire managed. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0268-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0268-02 |  |  |  |  | Administration area: continuous use: 6 workstations
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0268-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0268-02 |  |  |  |  | Administration area: continuous use: 6 workstations
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0268-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0268-02 |  |  |  |  | Administration area: continuous use: 6 workstations
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 12 |  |  | 12 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SCR026 |  | SCREEN, dividing, 1500H 2000W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 6 |  |  | 6 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 3 |  |  | 3 |  |  |  |  | CHA317 |  | CHAIR, upright, upholstered, stacking, wipeable | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | DES026 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1400W 700D | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | DRA057 |  | DRAWER UNIT, 3 drawer, lockable, on castors, desk height 715H 430W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | M0278-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0278-02 |  |  |  |  | Administration area: shared use: 6 workstations
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Clinical administration. 2) Computer workstation(s) may be used. 3) Telephone(s) may be used. 4) Files and records are stored. 5) Secure holding/storing of clothing and personal belongings. 6) Hanging outdoor clothing. 7) Information on computers may be accessed. 8) Printer may be used. 9) Electronic patient records (EPRs) may be accessed and updated. 10) Staff notices, information and/or messages may be displayed. 11) Dealing with enquiries. 12) Patient records may be reviewed and recorded. 13) Shredding documents.
| Personnel: | [6 empty] | 6 x staff. Up to 3 x others.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 30 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | The layout illustrates socket outlets at desk height because they should be easily accessible to enable equipment to be switched off for energy conservation. Floor box services are discouraged as they make it harder to convert the space into a clinical room in the future. It is therefore assumed that the workstations are wire managed. . Separate data and voice outlets may be used where structure cabling solutions are not available.
| ADB | [7 empty] | Room Environmental Data
M0278-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0278-02 |  |  |  |  | Administration area: shared use: 6 workstations
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300 |  | Over workstations
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 19
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
| General Notes: | [5 empty] | Refer to CIBSE Lighting Guide LG3 for areas with VDT’s
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 45
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 35 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Medium
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | M0278-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0278-02 |  |  |  |  | Administration area: shared use: 6 workstations
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Desirable - Project Option Clear glass with solar and privacy control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Non-essential - Project Option Designation to be validated against current documentation. HTM 57 (Mar-2005)
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | M0278-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | M0278-02 |  |  |  |  | Administration area: shared use: 6 workstations
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 12 |  |  | 12 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | OUT131 |  | SOCKET outlet data/voice, double. | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SCR026 |  | SCREEN, dividing, 1500H 2000W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BOA012 |  | BOARD, display/notice, wall mounted, 900H 600W | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BOA013 |  | BOARD, display/notice, wall mounted, 900H 1200W | [16 empty] | 2
| 6 |  |  | 6 |  |  |  |  | CHA301 |  | CHAIR, swivel, height adjustable, high back, with arms, wipeable, 5 star base, on castors | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | COM033 |  | COMPUTER KEYBOARD | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | COM049 |  | COMPUTER MONITOR, 17"; TFT, digital flat panel display, high-resolution screens, desk top | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | DES026 |  | DESK UNIT, cantilever, cable management, adjustable legs, modesty panel, 1400W 700D | [16 empty] | 3
| 18 |  |  | 18 |  |  |  |  | DRA056 |  | DRAWER UNIT, 2 drawer, lockable, on castors, 600H 410W 600D | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | DRA057 |  | DRAWER UNIT, 3 drawer, lockable, on castors, desk height 715H 430W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | P0625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | P0625 |  |  |  |  | Pantry/refreshment area
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Preparing beverages/snacks with patients. 2) Microwave oven may be used. 3) Small amounts of dry goods are stored in cupboard(s). 4) Provision of refrigerated storage. 5) Trays, crockery and cutlery are stored. 6) Disposal of waste and contaminated materials. 7) Hand-rinse basin may be used.
| Personnel: | [6 empty] | 1 - 2 x persons. Intermittent use.
| Planning Relationships: | [5 empty] | Located in staff, patient or visitors areas as appropriate.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following items are included on the room layout but are optional: - a microwave oven; - a dishwasher. The layout is suitable for ambulant/semi-ambulant users, consideration must be given to wheelchair user provision.
| ADB | [7 empty] | Room Environmental Data
P0625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | P0625 |  |  |  |  | Pantry/refreshment area
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | -
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Heat
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | P0625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | P0625 |  |  |  |  | Pantry/refreshment area
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | P0625
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | P0625 |  |  |  |  | Pantry/refreshment area
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS015 |  | BASIN, small, stainless steel, apron front, 1 tap hole, 500W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP703 |  | CUPBOARD, base, with door, on plinth, 900H 400W 500D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP715 |  | CUPBOARD, base, including sink panel, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CUP731 |  | CUPBOARD/DRAWER UNIT, base, with door, on plinth, 900H 600W 500D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CUP753 |  | CUPBOARD, upper, with door, 600H 600W 300D | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT049 |  | CONNECTION UNIT, switched, 13 amp, flex outlet | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT052 |  | CONNECTION UNIT, switched, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT301 |  | OUTLET, cold water for equipment | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT341 |  | OUTLET, drainage, anti-syphon | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP359 |  | TAP, pillar, high neck, long lever, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WAT003 |  | WATER BOILER, 2.5 litre, electric, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WRT237 |  | WORKTOP, dished, stainless steel, with integral left of centre sink bowl and 2 tap holes, 3500W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS007 |  | DISPENSER, paper towel roll, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | WAS065 |  | DISHWASHER, under bench, high temperature | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | OVE013 |  | OVEN, microwave, heavy duty, 1600watt, capacity 26 litre, 370H 465W 560D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | REF058 |  | REFRIGERATOR, capacity 160 litre, automatic defrost, stainless steel, underbench, external temperature gauge, lockable, on castors, 850H 610W 600D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | P0808
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | P0808 |  |  |  |  | Vending machines
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Buying cold snacks/beverages from vending machines.
| Personnel: | [6 empty] | Intermittent use.
| Planning Relationships: | [5 empty] | Adjacent to main waiting area. Adjacent to main entrance & concourse area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 3 |  |  |  |  | Height (mm): |  |  |  | 2400
2400 mm is the anticipated minimum ceiling height. Should be sized to suit surrounding area/design.
Notes:
| ADB | [7 empty] | Room Environmental Data
P0808
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | P0808 |  |  |  |  | Vending machines
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 21
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
| Supply Air: Final Filter Class | [12 empty] | -
Permisiible Relative Humidity Range (%):
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 60
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | P0808
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | P0808 |  |  |  |  | Vending machines
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Not required - open to circulation area or part of another space
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | P0808
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | P0808 |  |  |  |  | Vending machines
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | OUT002 |  | OUTLET cable, 13 amp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT054 |  | CONNECTION UNIT, unswitched, 13 amp, neon indicator | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT301 |  | OUTLET, cold water for equipment | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOL006 |  | HOLDER, sack, with lid foot operated, medium, freestanding, 875H 430W 385D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | VEN001 |  | VENDING MACHINE, cold snacks | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | VEN002 |  | VENDING MACHINE, hot/cold drinks | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0554
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0554 |  |  |  |  | Staff communal changing room: 20 lockers
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) User may undress and dress. 2) Changing into clean uniforms (including blues or greens). 3) Changing footwear. 4) Secure hanging of wet outdoor clothing. 5) Secure holding/storing of clothing and personal belongings. 6) Secure holding/storage of motorcycle and bicycle helmets. 7) Hanging outdoor clothing. 8) Disposal of dirty uniforms.
| Personnel: | [6 empty] | Up to 6 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Direct access to showers and/or individual changing room(s). Close to WCs. Close to uniform exchange, if provided.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 20 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | It is assumed that this space is supported by one individual changing room. See V0725 for details of semi-ambulant individual changing room and V0276 for independent wheelchair individual changing room. The room layout illustrates space for all users but includes lockers for generally ambulant users. A suitable number of lockers must comply with the requirements of BS8300/ADM for wheelchair users depending upon the expected user group. The following items may be provided: - cube lockers for personal belongings will be required if staff are not allocated their own changing lockers; - shaver sockets, shelves and lights associated with mirrors.
| ADB | [7 empty] | Room Environmental Data
V0554
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0554 |  |  |  |  | Staff communal changing room: 20 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0554
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0554 |  |  |  |  | Staff communal changing room: 20 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 2 sets of doors: 2 x personnel, wheelchair & equipment access (1000mm)
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0554
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0554 |  |  |  |  | Staff communal changing room: 20 lockers
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 3 |  |  | 3 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | CHA383 |  | CHAIR, stacking, polypropylene, with back and seat pads, wipeable. | [16 empty] | 3
| 20 |  |  | 20 |  |  |  |  | LOC005 |  | LOCKER clothes, single, 1800H 300W 550D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC154 |  | RACK shoe, (bridge unit base between lockers assembly) 175H 1200W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAI023 |  | RAIL, coat hanging, 20 secure hangers with sleeve lock chain, (bridge unit top between lockers assembly), 1200W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0554-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0554-02 |  |  |  |  | Staff communal changing room: 10 lockers
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) User may undress and dress. 2) Changing into clean uniforms (including blues or greens). 3) Changing footwear. 4) Secure hanging of wet outdoor clothing. 5) Secure holding/storing of clothing and personal belongings. 6) Secure holding/storage of motorcycle and bicycle helmets. 7) Hanging outdoor clothing. 8) Disposal of dirty uniforms.
| Personnel: | [6 empty] | Up to 4 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Direct access to showers and/or individual changing room(s). Close to WCs. Close to uniform exchange, if provided.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 11 |  |  |  |  | Height (mm): |  |  |  | 2700
.
| Notes: | [7 empty] | It is assumed that this space is supported by one individual changing room. See V0725 for details of semi-ambulant individual changing room and V0276 for independent wheelchair individual changing room. The room layout illustrates space for all users but includes lockers for generally ambulant users. A suitable number of lockers must comply with the requirements of BS8300/ADM for wheelchair users depending upon the expected user group. The following items may be provided: - cube lockers for personal belongings will be required if staff are not allocated their own changing lockers; - shaver sockets, shelves and lights associated with mirrors.
| ADB | [7 empty] | Room Environmental Data
V0554-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0554-02 |  |  |  |  | Staff communal changing room: 10 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0554-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0554-02 |  |  |  |  | Staff communal changing room: 10 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0554-02
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0554-02 |  |  |  |  | Staff communal changing room: 10 lockers
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CHA383 |  | CHAIR, stacking, polypropylene, with back and seat pads, wipeable. | [16 empty] | 3
| 10 |  |  | 10 |  |  |  |  | LOC005 |  | LOCKER clothes, single, 1800H 300W 550D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAC154 |  | RACK shoe, (bridge unit base between lockers assembly) 175H 1200W 450D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | RAI023 |  | RAIL, coat hanging, 20 secure hangers with sleeve lock chain, (bridge unit top between lockers assembly), 1200W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0554-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0554-03 |  |  |  |  | Staff communal changing room: 30 lockers
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) User may undress and dress. 2) Changing into clean uniforms (including blues or greens). 3) Changing footwear. 4) Secure hanging of wet outdoor clothing. 5) Secure holding/storing of clothing and personal belongings. 6) Secure holding/storage of motorcycle and bicycle helmets. 7) Hanging outdoor clothing. 8) Disposal of dirty uniforms.
| Personnel: | [6 empty] | Up to 12 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Direct access to showers and/or individual changing room(s). Close to WCs. Close to uniform exchange, if provided.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 30 |  |  |  |  | Height (mm): |  |  |  | 2700
| Notes: | [7 empty] | It is assumed that this space is supported by one individual changing room. See V0725 for details of semi-ambulant individual changing room and V0276 for independent wheelchair individual changing room. The room layout illustrates space for all users but includes lockers for generally ambulant users. A suitable number of lockers must comply with the requirements of BS8300/ADM for wheelchair users depending upon the expected user group. The following items may be provided: - cube lockers for personal belongings will be required if staff are not allocated their own changing lockers; - shaver sockets, shelves and lights associated with mirrors.
| ADB | [7 empty] | Room Environmental Data
V0554-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0554-03 |  |  |  |  | Staff communal changing room: 30 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | S/E
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0554-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0554-03 |  |  |  |  | Staff communal changing room: 30 lockers
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02
| Windows: | [5 empty] | Non-essential - Project Option Obscured glass with solar control Designation to be validated against current documentation (HTM 55 archived).
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0554-03
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0554-03 |  |  |  |  | Staff communal changing room: 30 lockers
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 4 |  |  | 4 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 4 |  |  | 4 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 6 |  |  | 6 |  |  |  |  | CHA383 |  | CHAIR, stacking, polypropylene, with back and seat pads, wipeable. | [16 empty] | 3
| 30 |  |  | 30 |  |  |  |  | LOC005 |  | LOCKER clothes, single, 1800H 300W 550D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | RAC154 |  | RACK shoe, (bridge unit base between lockers assembly) 175H 1200W 450D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | RAI023 |  | RAIL, coat hanging, 20 secure hangers with sleeve lock chain, (bridge unit top between lockers assembly), 1200W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Semi-ambulant person may undress/dress in privacy. 2) Hanging outdoor clothing. 3) Call systems may be used.
| Personnel: | [6 empty] | 1 x person. Intermittent use.
| Planning Relationships: | [5 empty] | Adjacent to sub-waiting area (if provided). Close to WC facilities. May be use in conjunction with staff changing area.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items are shown on the room layout but are optional: - patient/staff call (although required when for patient use); The following items may be provided: - a tip-up seat
| ADB | [7 empty] | Room Environmental Data
V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 6
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | heat to be considered if adjacent to shower rooms
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0725
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0725 |  |  |  |  | Changing room: semi-ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | CAL006 |  | PULL CORD, patient/staff call (help) with reassurance lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SEA004 |  | SEAT, bench, wall mounted, 480H 1300W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V0922
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0922 |  |  |  |  | WC: independent wheelchair
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Independent wheelchair accessible toilet and adjacent hand-rinse basin may be used. 2) Call systems may be used.
| Personnel: | [6 empty] | 1 x person. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 4.5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The call repeat lamp is situated over the door outside the room. The following items are shown on the drawing but are optional: - the bin for the disposal of sanitary towels is only required in female WCs;
| ADB | [7 empty] | Room Environmental Data
V0922
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0922 |  |  |  |  | WC: independent wheelchair
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 20
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V0922
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0922 |  |  |  |  | WC: independent wheelchair
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, wheelchair & equipment access (1000mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V0922
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V0922 |  |  |  |  | WC: independent wheelchair
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAC002 |  | BACKREST, WC/toilet, padded, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL006 |  | PULL CORD, patient/staff call (help) with reassurance lamp | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL007 |  | PULL/PUSH BUTTON, staff emergency call, reset and integral/adjacent indicator lamp | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | CAL012 |  | RESET UNIT, with repeat lamp, patient/staff call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CAL034 |  | LAMP, repeat call, patient/staff or staff emergency or cardiac call | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CIS005 |  | CISTERN WC/toilet, concealed, reversible. To suit WC | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR026 |  | MIRROR, unbreakable, wall mounted, 1300H 500W | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | RAI048 |  | RAIL, grab, vertical, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI159 |  | RAIL, grab, horizontal, with supports, wall mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI161 |  | RAIL, grab, horizontal, wall or door mounted, 600mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI172 |  | RAIL, grab, hinged, wall mounted, 650mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WCH005 |  | WC/toilet pan with seat, 700 mm projection, hospital pattern, rimless pan, vitreous china. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS015 |  | DISPENSER, toilet paper, dispense individual sheets, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE100 |  | SHELF, raised edge, non-breakable, 600W 200D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE102 |  | SHELF, raised edge, non-breakable, 200W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | VEN003 |  | VENDING MACHINE, sanitary towel with coin slot | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN028 |  | BIN, disposal, sealed, operated with one hand, nominal 420H 155W 490D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL003 |  | HOLDER, sack, small, freestanding | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Toilet may be used by ambulant person. 2) Hand-rinse basin may be used.
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
Planning Relationships:
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | The following items are shown on the drawing but are optional: - the bin for the disposal of sanitary towels is only required in female WCs; - the shelf next to the basin.
| ADB | [7 empty] | Room Environmental Data
V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 20
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V1010
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V1010 |  |  |  |  | WC: ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | BAS105 |  | BASIN, small, general pattern, vitreous china, 1 tap right hand hole, no overflow, bottom outlet, 400W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CIS005 |  | CISTERN WC/toilet, concealed, reversible. To suit WC | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP289 |  | TAP, monobloc, pillar mixer, integral thermostatic, short lever. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | WCH001 |  | WC/toilet pan with seat, 520-550 projection, hospital pattern, rimless pan, vitreous china. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS024 |  | DISPENSER, soap, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | HOL016 |  | HOLDER, toilet roll, multi, large | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | BIN028 |  | BIN, disposal, sealed, operated with one hand, nominal 420H 155W 490D | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL004 |  | HOLDER, sack, with lid foot operated, small, freestanding | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Shower may be used by ambulant person. 2) User may undress and dress in privacy. 3) Hanging outdoor clothing. 4) Hanging clothes and towels.
| Personnel: | [6 empty] | 1 x person (staff or visitor). Intermittent use.
| Planning Relationships: | [5 empty] | Associated with staff changing area. Close to a WC.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2.5 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | This room is not recommended for patient use. The following items may be provided: - inward opening door; - full length mirror.
| ADB | [7 empty] | Room Environmental Data
V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 22
| Minimum Air Changes (AC/hr): | [13 empty] | 10
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 100-150
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Moderate |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 43
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [15 empty] | Omitted via risk assessment
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel access (900mm) - see HBN 00-02 Requirement for hinge protection when areas used by children
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | V1321
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | V1321 |  |  |  |  | Shower room: ambulant
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | DIS200 |  | DISH, soap, wall mounted | [16 empty] | 1
| 3 |  |  | 3 |  |  |  |  | HOO019 |  | HOOK, single, small, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | LIG063 |  | LUMINAIRE, single fluorescent lamp, wall, 8 watt, 300 mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | MIR002 |  | MIRROR, wall mounted, 900H 300W | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT025 |  | SOCKET outlet, shaver | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | RAI260 |  | RAIL for shower curtain, 1000mm | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SEA024 |  | SEAT, tip-up, wall mounted, 400 W 400D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO009 |  | SHOWER TRAY ceramic slip resistant base, with drainage outlet, 800W 800D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO018 |  | SHOWER, valve, thermostatic mixer (associated with SHO020). | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHO020 |  | SHOWER, adjustable shower head hand spray (associated with SHO018). | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC014 |  | SWITCH 5amp ac single pole, 1 way, ceiling pull cord | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SHE101 |  | SHELF, raised edge, non-breakable, 300W 150D | [16 empty] | 2
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W0615
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | W0615 |  |  |  |  | Store: protective clothing
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Holding clean protective laboratory coats.
Personnel:
| Planning Relationships: | [5 empty] | Convenient to locker rooms.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 2 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | Protective clothing (white coats) to be worn by those working in laboratories (inc. maintenance staff) & any visitors.
| ADB | [7 empty] | Room Environmental Data
W0615
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | W0615 |  |  |  |  | Store: protective clothing
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
| Supply Air: Final Filter Class | [12 empty] | G4
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | S/N
| Daytime General Service Illuminance (Lux): | [13 empty] | 300
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 55
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Low
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W0615
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | W0615 |  |  |  |  | Store: protective clothing
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W0615
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | W0615 |  |  |  |  | Store: protective clothing
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 3 |  |  | 3 |  |  |  |  | SHE073 |  | SHELF, slatted, horizontal, adjustable, 1500W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | STO008 |  | STOOL, kick, retractable castors | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | W1598
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | W1598 |  |  |  |  | External store: flammable goods
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Flammable liquids are stored safely and securely. 2) Issuing working stock quantities. 3) Manoeuvring hand trucks, trolleys and mobile racks.
| Personnel: | [6 empty] | 1-2 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | External - away from public areas. Store should be sited away from any entrances, including the external goods entrance and emergency exits.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2400
| Notes: | [7 empty] | All electrical equipment to be sealed and constructed of self-extinguishing materials sufficient to comply with statutory requirements and HTM 05 (all relevant parts) for use within rooms containing flammable goods. Statutory notices on outside of outward opening metal door.
| ADB | [7 empty] | Room Environmental Data
W1598
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | W1598 |  |  |  |  | External store: flammable goods
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 4
| Ventilation Type: | [13 empty] | S/E/N
| Pressure Relative to Adjoining Space: | [13 empty] | Bal or -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
Type Of Control:
Daytime General Service Illuminance (Lux):
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | N
Colour Rendering Required Characteristics (Ra):
Unified Glare Rating Limit (UGRL):
| Emergency Escape Route Lighting Required: | [13 empty] | Y
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | -
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [15 empty] | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [15 empty] | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
Room Sound-insulation Parameters - Noise Generation:
Noise Sensitiviy:
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke |  | consider ionisation detector
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | W1598
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | W1598 |  |  |  |  | External store: flammable goods
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset - metal: 1 x personnel, trolley, & equipment access (1900mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | W1598
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | W1598 |  |  |  |  | External store: flammable goods
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | DOR226 |  | Doorset,metal, 1900mm
| 6 |  |  | 6 |  |  |  |  | SHE063 |  | SHELF, adjustable, P.V.C. coated steel, perforated, wall mounted, 1500W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC027 |  | SWITCH, light, external | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CUP006 |  | CUPBOARD, flammable material, metal, lockable, liquid retaining shelf, floor standing, 915H 460W 485D | [16 empty] | 3
| 2 |  |  | 2 |  |  |  |  | RAC320 |  | RACK, freestanding, 4 tier, 1700H 1800W 450D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y0646
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | Y0646 |  |  |  |  | Disposal hold: 3000 litres
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Holding domestic, clinical and recyclable waste for disposal or reprocessing
| Personnel: | [6 empty] | 1 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Adjacent to main circulation route.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 12 |  |  |  |  | Height (mm): |  |  |  | 2700
Ceiling height must allow bin lids to open fully.
| Notes: | [7 empty] | Separate bins/areas must be provided for: - clinical waste; - domestic waste; - recyclable items; - linen; - equipment requiring reprocessing.
| ADB | [7 empty] | Room Environmental Data
Y0646
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | Y0646 |  |  |  |  | Disposal hold: 3000 litres
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 80
| Unified Glare Rating Limit (UGRL): | [13 empty] | 22
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
Standby Lighting Grade - General Lighting:
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 40 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Smoke
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y0646
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | Y0646 |  |  |  |  | Disposal hold: 3000 litres
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel, trolley & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y0646
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | Y0646 |  |  |  |  | Disposal hold: 3000 litres
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT010 |  | SOCKET outlet, switched, 13 amp, twin | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | BIN037 |  | BIN wheelie, 770 litre, 1360H1360W 800D | [16 empty] | 3
| ADB | [8 empty] | Room Data Sheet | [11 empty] | Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [16 empty] | Revision Date: | [5 empty] | 05/04/2013
| Activities: | [5 empty] | 1) Disposal of liquid waste. 2) Filling and emptying cleaning equipment and containers. 3) Holding/storing cleaning equipment. 4) Cleaning equipment may be parked and/or stored. 5) Hand-rinse basin may be used. 6) Sink may be used. 7) Janitorial unit may be used.
| Personnel: | [6 empty] | 2 x staff. Intermittent use.
| Planning Relationships: | [5 empty] | Close to areas served.
| Space Data: | [6 empty] | Area (m²): |  |  |  | 8 |  |  |  |  | Height (mm): |  |  |  | 2400
If large equipment is stored elsewhere, the size of this room can be reduced.
| Notes: | [7 empty] | This room represents a typical traditional cleaners' room with space for storing a vacuum cleaner, scrubbing/polishing machine (for hard floors) and mop and bucket (stored on the cleaners' trolley). It includes a combined bucket sink and hand-rinse basin (janitorial unit) and separate sink. The following items are shown on the room layout but are optional: - small cube lockers.
| ADB | [7 empty] | Room Environmental Data
Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| TEMPERATURE AND VENTILATION | [11 empty] | Requirements
Notes
| Permissible Space Temerature Range(dry bulb) (degC): | [13 empty] | 18 - 28
| Heating Design Temperature (dry bulb)(degC): | [13 empty] | 18
| Minimum Air Changes (AC/hr): | [13 empty] | 3
| Ventilation Type: | [13 empty] | E
| Pressure Relative to Adjoining Space: | [13 empty] | -ve
Supply Air: Final Filter Class
| Permisiible Relative Humidity Range (%): | [13 empty] | Uncontrolled
General Notes:
LIGHTING
| Type Of Control: | [13 empty] | N
| Daytime General Service Illuminance (Lux): | [13 empty] | 200
Daytime Specific Service Illuminance (Lux):
Nighttime General Service Illuminance (Lux):
Nighttime Specific Service Illuminance (Lux):
Local Task Illuminance (Lux):
| Colour Rendering Required: | [14 empty] | Y
| Colour Rendering Required Characteristics (Ra): | [13 empty] | 22
| Unified Glare Rating Limit (UGRL): | [13 empty] | 80
| Emergency Escape Route Lighting Required: | [13 empty] | Y |  | In accordance with BS 5266 and Health Technical Memorandums
| Standby Lighting Grade - General Lighting: | [13 empty] | B
Standby Lighting Grade - Local Lighting:
General Notes:
RISK
Clinical Risk Category:
Non-clinical Business Continuity Risk Category:
General Notes:
NOISE
| Noise Intrusion (dB) 1hr day: | [13 empty] | 50
| Noise Intrusion (dB) 1hr night: | [13 empty] | -
| Noise Intrusion (dB) f night: | [13 empty] | -
| Maximum Internal Noise from M&E Services (NR): | [13 empty] | 45 |  | Total noise of MEP services under normal operation across the range 63Hz to 4kHz inclusive.
| Room Sound-insulation Parameters - Privacy: | [13 empty] | Not Private |  | Reference to Table 3 of the Department of Health 'Acoustics: Technical design manual 4032:0.6:England'.
| Room Sound-insulation Parameters - Noise Generation: | [13 empty] | Typical
| Noise Sensitiviy: | [13 empty] | Not Sensitive
Sound-insulation Rating (dB D nT,w):
General Notes:
SAFETY/FIRE
| Maximum Surface Temperature (DegC): | [13 empty] | 82
| Domestic Hot Water Discharge Temperature (DegC): | [13 empty] | 41/>55
| Maximum Cold Water Discharge Temperature (DegC): | [13 empty] | <20
General Notes:
| Type of Automatic Fire Detection: | [13 empty] | Heat
General Notes:
| ADB | [7 empty] | Room Design Character | [12 empty] | Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [17 empty] | Revision Date: | [5 empty] | 05/04/2013
| Walls: | [5 empty] | Wall finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Wall finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Floor: | [5 empty] | Floor finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Floor finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
Ceiling:
Ceiling finishes to comply with Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England. Ceiling finishes to be selected using the "Selection Procedure for Finishes" included in 8941:06: England.
| Doorsets: | [5 empty] | Configuration, glazing, fire rating, security, etc. to be determined by Project Team. HTM 58 (Mar-2005) Refer to HBN 00-04 (May-2007) for effective clear door widths. 1 doorset: 1 x personnel & equipment access (1500mm)
| Windows: | [5 empty] | Not required
Internal Glazing:
Not required
| Hatch: | [5 empty] | Not required
Notes:
All finishes selected must have an appropriate risk assessment to accompany the design decision. Infection Control must be consulted as described in Performance Requirements for Building Elements Used in Healthcare Facilities 8941:0.6 England.
| ADB |  |  |  |  | Schedule of Components by Room | [15 empty] | Y1510
| Project: | [5 empty] | ADB2013 |  |  |  |  | Activity Database version 2013 © Crown Copyright
| Department: | [5 empty] | HBN15 |  |  |  |  | Facilities for pathology services - list of spaces
| Room: | [5 empty] | Y1510 |  |  |  |  | Cleaners' room
| Room Number: | [18 empty] | Revision Date: | [5 empty] | 05/04/2013
|  | Quantity | [20 empty] | Alt. Code | [5 empty] | Grp
New |  |  | Trans |  | Total |  |  |  | Code |  |  | Description
| 2 |  |  | 2 |  |  |  |  | HOO020 |  | HOOK, single, large, wall mounted | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | OUT005 |  | SOCKET outlet, switched, 13 amp, single | [16 empty] | 1
| 2 |  |  | 2 |  |  |  |  | SHE231 |  | SHELF, 1500W 300D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SIN013 |  | SINK and BASIN combination Janitorial unit, hinged bucket grating to sink and monobloc mixer tap with swivel nozzle, stainless steel, 900H 500W 600D. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SNU012 |  | SINK UNIT, single bowl with right hand drainer, no tap holes, 1200W 600D | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | SWC025 |  | SWITCH, light | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | TAP809 |  | TAP, bib, lever, hospital pattern, pair hot and cold, 1/2 in. | [16 empty] | 1
| 1 |  |  | 1 |  |  |  |  | CLI017 |  | CLIP, spring, 32mm dia. 3, mounted on a wooden batten, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS013 |  | DISPENSER, paper towel, wall mounted | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | DIS030 |  | DISPENSER, soap, disposable single cartridge, lever action, wall mounted | [16 empty] | 2
| 2 |  |  | 2 |  |  |  |  | LOC012 |  | LOCKER, wall mounted, 340H 300W 300D | [16 empty] | 2
| 1 |  |  | 1 |  |  |  |  | CLE008 |  | SCRUBBING/POLISHING MACHINE, single brush, 110v machine | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | CLE018 |  | CLEANER VACUUM, dry suction, tub, with accessories, filtered air exhaust | [16 empty] | 3
| 6 |  |  | 6 |  |  |  |  | CON061 |  | CONE, warning, 'wet floor' | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | HOL014 |  | HOLDER, sack, with lid foot operated, large, capacity 120 litre, mobile | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | LAD002 |  | LADDER, 3 tread, platform type 750mm height, folding | [16 empty] | 3
| 1 |  |  | 1 |  |  |  |  | TRO068 |  | TROLLEY, cleaners, mop bucket, 3 shelves tray and waste sack holder, 980H 1170W 550D | [16 empty] | 3
Activity DataBase
2016-12-29