## Title Page
Neighbourhood Health Centres
Design Typologies - Schedules of Accommodation
30k GP Population - Basis for the designs
Date: | 2026-04-15
Version number: 1.0

## Assumptions
Note: The schedule and assumptions are iterative, are based on the information available to date and therefore are subject to change.
No. | Category | Assumption
1 | ALL | Functional content is indicative and based on the current iteration of the activity model. Functional content reflects the following assumptions for the unintegrated and integrated models respectively: • Both models reflect the modelled requirements for a GP population of 30,000, a Community Care population of 50,000, and an 'Other' (e.g. diagnostics etc.) of 100,000. • The unintegrated model is set to the following parameters: 50 operational hours per week, 50 operational weeks per annum, with the majority of services operating at 60% utilisation (Secondary care, community care and Minor Injuries assumed to operate at 80% utilisation). • The integrated model is set to the following parameters: 72 operational hours per week, 50 operational weeks per annum for Frailty and GP services, with all other services operating for 52 weeks per annum, and all services operating at 80% utilisation.
2 | ALL | Where available, all standard room sizes have been aligned with the updated HBN 00-03 and HBN 11-01.
3 | ALL | Consultation/examination and Consultation/treatment rooms have been planned based on a ratio of 80:20; in some cases, this has been rounded up/down to support the design. Treatment rooms have been based on a ratio of 70:30 Standard: Bariatric.
4 | ALL | The following departmental uplifts have been assumed based on updated guidance and recent project experience: • Circulation: 35% for clinical areas, including clinical and non-clinical support zones, and 25% for non-clinical areas (i.e. staff and public zones) • Engineering: Has been standardised at 5% for all services • Planning: Has been standardised at 11% for all services The following whole building uplifts have been assumed: • Communication: Has been standardised at 12% for all services • Plant: Has been standardised at 23% for all services
5 | ALL | The unintegrated schedule is based on the following assumptions: • Where clinical activity/specificity permits, services have been briefed as a distinct service zone and/or department (e.g. GP services, some aspects of CMH). • Where appropriate, some services may share clinical and non-clinical support functions and/or staff support areas to reduce the unnecessary duplication of space. This has been assumed for services with high potential of cross-MDT collaboration and/or where low service activity does not justify the service as being a distinct(i.e. separate) department. • Where appropriate, some services may share waiting/reception functions to reduce the unnecessary duplication of reception/public amenities. This has been assumed for services with patients of similar acuity/need and where there is a high potential of cross-MDT collaboration. Where adult and paediatric services are provided, flows should be separated and discrete/separate waiting areas should be provided. • Whilst services may share some support functions, the schedule has assumed distinct clinical zones for each service which comprise of key clinical functional content based on the activity model (i.e. clinical rooms are not shared). The integrated schedule is based on the following assumptions: • Generic clinical rooms will be shared by all services such that no one service will 'own' a space. It is recognised that some services (based on national requirements and/or to support patient safety, experience) may require speciality-specific accommodation and/or a distinct zone (e.g. mental health services). The nuances of an integrated model/schedule will be worked through in later iterations. • All services will share waiting spaces, clinical and non-clinical support functions, and staff support areas (where appropriate) to support a truly integrated model. Where paediatric services and adult services are provided, flows should be appropriately separated either through the design or through list planning.
6 | Virtual consultation allowance | The number of virtual consultation booths provided is based on the modelling, and assumes 70% of the modelled output will be carried out within dedicated virtual consultation booths, and 30% will be carried out within quiet rooms in the Staff zone.
7 | Staff administration allowance | The schedule assumes 0.5 x hot desk per generic clinical room (including group rooms and phlebotomy (where provided)) for core services, and 0.6 x hot desk per generic clinical room for core+ and core++ models. It is assumed 20% of admin may be carried out within clinical spaces based on the 80% assumed room utilisation and 20% may be carried out within touchdown spaces. Staff may also utilise the collaboration area, quiet room(s) and interview rooms for administrative functions.
8 | Staff administration allowance | The schedule does not assume/provide clinical touchdown spaces for staff in the unintegrated model due to the lower utilisation / reduced assumed movement of staff between rooms. Staff may utilise the hot desks provided, otherwise it is assumed staff will write up clinical notes/carry out essential clinical admin within the generic clinical room in between clinic sessions.
9 | Staff administration allowance | The schedule assumes/provides clinical touchdown spaces for staff in the integrated model(s) only. It is assumed given the integrated nature, sharing of rooms and higher utilisation of this model, staff will require additional touchdown spaces to write up clinical notes/carry out essential admin in between clinic sessions - an uplift of 20% (based on number of clinical rooms) has been provided.
10 | Staff welfare and support allowance | The schedule assumes 40% occupancy for staff rest areas, based on the assumed number of staff working with 10% (rounded up) of this being provided as wheelchair places.
11 | Staff welfare and support allowance | The schedules assumes 1 x per person allowance for staff changing/shower/lockers per generic clinical room, including group rooms and phlebotomy (where provided).
12 | Waiting allowance | The schedule assumes 2 x people waiting per generic clinical room, and 8 people waiting per group room. A separate children's/play area allowance has been included, and is based on either 10% of the total waiting allowance (rounded up) or a minimum of 6m2 has been provided, whichever is larger.
13 | Reception / Self-check-in allowance | The number of reception desk spaces / self-check-in kiosks have been based on an allocation of 1 per 35 people waiting. In some cases, e.g. mental health, self-check-in kiosks have been omitted.

## Summary Sheet
1a) Unintegrated - Core | [7 empty] | 2a) Integrated - Core
|  |  |  | Departmental Uplifts | [7 empty] | Departmental Uplifts
Service | Zone | Key Functional Content | NDA (m2) | Planning | Circulation | Engineering | GDA(m2) | Service | Zone | Key Functional Content | NDA (m2) | Planning | Circulation | Engineering | GDA(m2)
Main Entrance | Public |  | 59 | 11% | 25% | 5% | 83.19 | Main Entrance | Public |  | 281 | 11% | 25% | 5% | 396.21
GP Services | Public |  | 231 | 11% | 25% | 5% | 325.71 | Clincal Zone | Clinical |  | 496.7 | 11% | 35% | 5% | 750.017
| Clinical |  | 486 | 11% | 35% | 5% | 733.86 | Clinical and Non-clinical Support | Clinical and Non-clinical Support |  | 133 | 11% | 35% | 5% | 200.83
| Clinical and Non-clinical Support |  | 72 | 11% | 35% | 5% | 108.72 | Hot Zone | Clinical |  | 26.5 | 11% | 35% | 5% | 40.015
| Hot zone |  | 26.5 | 11% | 35% | 5% | 40.015 | Staff Support | Staff Support |  | 290.2 | 11% | 25% | 5% | 409.182
| Staff Support |  | 255.55 | 11% | 25% | 5% | 360.3255 | [6 empty] | Subtotal | 1796.254
Community Care & Secondary Shift Clinics | Public |  | 151.5 | 11% | 25% | 5% | 213.615 | Building uplifts |  |  |  |  | Communication | 12% | 215.5505
| Community Care - Clinical |  | 147.5 | 11% | 35% | 5% | 222.725 | [5 empty] | Plant | 23% | 413.1384
| Secondary Shift - Clinical |  | 99.8 | 11% | 35% | 5% | 150.698 | [6 empty] | Total GIA | 2424.9429
| Communiy & Secondary - Shared Clinical |  | 113 | 11% | 35% | 5% | 170.63 | [6 empty] | As-drawn GIA | 2488.4
| Clinical and Non-clinical Support |  | 74 | 11% | 35% | 5% | 111.74 | [6 empty] | % variation | 2.617%
| Staff Support |  | 172.4 | 11% | 25% | 5% | 243.084
FM Hub | Non-clinical support |  | 28 | 11% | 25% | 5% | 39.48
[6 empty] | Subtotal | 2803.7925
Building uplifts |  |  |  |  | Communication | 12% | 336.4551
[5 empty] | Plant | 23% | 644.8723
[6 empty] | Total GIA | 3785.1199
1b) Unintegrated - Core + | [7 empty] | 2b) Integrated - Core +
|  |  |  | Departmental Uplifts | [7 empty] | Departmental Uplifts
Service | Zone | Key Functional Content | NDA (m2) | Planning | Circulation | Engineering | GDA(m2) | Service | Zone | Key Functional Content | NDA (m2) | Planning | Circulation | Engineering | GDA(m2)
Main Entrance / Wider Neighbourhood Support | Public |  | 112 | 11% | 25% | 5% | 157.92 | Main Entrance | Public |  | 428 | 11% | 25% | 5% | 603.48
| Staff |  | 29 | 11% | 25% | 5% | 40.89 | Clincal Zone | Clinical |  | 726.3 | 11% | 35% | 5% | 1096.713
GP Services | Public |  | 231 | 11% | 25% | 5% | 325.71 | Clinical and Non-clinical Support | Clinical and Non-clinical Support |  | 229 | 11% | 35% | 5% | 345.79
| Clinical |  | 486 | 11% | 35% | 5% | 733.86 | Hot Zone | Clinical |  | 26.5 | 11% | 35% | 5% | 40.015
| Clinical and Non-clinical Support |  | 72 | 11% | 35% | 5% | 108.72 | Staff Support | Staff Support |  | 482.9 | 11% | 25% | 5% | 680.889
| Hot zone |  | 26.5 | 11% | 35% | 5% | 40.015 | [6 empty] | Subtotal | 2766.887
| Staff Support |  | 255.55 | 11% | 25% | 5% | 360.3255 | Building uplifts |  |  |  |  | Communication | 12% | 332.0264
Community Care, Secondary Shift Clinics & Family Hub | Community & Secondary - Public |  | 158.5 | 11% | 25% | 5% | 223.485 | [5 empty] | Plant | 23% | 636.384
| Family Hub - Public |  | 77.5 | 11% | 25% | 5% | 109.275 | [6 empty] | Total GIA | 3735.2975
| Family Hub - Clinical |  | 136.5 | 11% | 35% | 5% | 206.115 | [6 empty] | As-drawn GIA | 3732.5
| Community Care - Clinical |  | 147.5 | 11% | 35% | 5% | 222.725 | [6 empty] | % variation | -0.07489%
| Secondary Shift - Clinical |  | 99.8 | 11% | 35% | 5% | 150.698
| Communiy & Secondary - Shared Clinical |  | 113 | 11% | 35% | 5% | 170.63
| Clinical and Non-clinical Support |  | 81 | 11% | 35% | 5% | 122.31
| Staff Support |  | 245.4 | 11% | 25% | 5% | 346.014
Community Mental Health & Minor Injuries/Walk-in | Community Mental Health - Public |  | 65 | 11% | 25% | 5% | 91.65
| Minor Injuries - Public |  | 46.5 | 11% | 25% | 5% | 65.565
| Community Mental Health - Clinical |  | 106.5 | 11% | 35% | 5% | 160.815
| Minor Injuries - Clinical |  | 154 | 11% | 35% | 5% | 232.54
| Clinical and Non-clinical Support |  | 82 | 11% | 35% | 5% | 123.82
| Staff Support |  | 134.3 | 11% | 25% | 5% | 189.363
FM Hub | Non-clinical support |  | 38 | 11% | 25% | 5% | 53.58
[6 empty] | Subtotal | 4236.0255
Building uplifts |  |  |  |  | Communication | 12% | 508.3231
[5 empty] | Plant | 23% | 974.2859
[6 empty] | Total GIA | 5718.6344
1c) Unintegrated - Core ++ | [7 empty] | 2c) Integrated - Core ++
|  |  |  | Departmental Uplifts | [7 empty] | Departmental Uplifts
Service | Zone | Key Functional Content | NDA (m2) | Planning | Circulation | Engineering | GDA(m2) | Service | Zone | Key Functional Content | NDA (m2) | Planning | Circulation | Engineering | GDA(m2)
Main Entrance / Wider Neighbourhood Support | Public |  | 118 | 11% | 25% | 5% | 166.38 | Main Entrance | Public |  | 469 | 11% | 25% | 5% | 661.29
| Staff Support |  | 29 | 11% | 25% | 5% | 40.89 | Clincal Zone | Clinical |  | 809.9 | 11% | 35% | 5% | 1222.949
GP Services | Public |  | 231 | 11% | 25% | 5% | 325.71 | Clinical and Non-clinical Support | Clinical and Non-clinical Support |  | 301 | 11% | 35% | 5% | 454.51
| Clinical |  | 486 | 11% | 35% | 5% | 733.86 | Hot Zone | Clinical |  | 26.5 | 11% | 35% | 5% | 40.015
| Clinical and Non-clinical Support |  | 72 | 11% | 35% | 5% | 108.72 | Staff Support | Staff Support |  | 576 | 11% | 25% | 5% | 812.16
| Hot zone |  | 26.5 | 11% | 35% | 5% | 40.015 | [6 empty] | Subtotal | 3190.924
| Staff Support |  | 255.55 | 11% | 25% | 5% | 360.3255 | Building uplifts |  |  |  |  | Communication | 12% | 382.9109
Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Community & Secondary - Public |  | 191.5 | 11% | 25% | 5% | 270.015 | [5 empty] | Plant | 23% | 733.9125
| Family Hub - Public |  | 77.5 | 11% | 25% | 5% | 109.275 | [6 empty] | Total GIA | 4307.7474
| Family Hub - Clinical |  | 136.5 | 11% | 35% | 5% | 206.115 | [6 empty] | As-drawn GIA | 4315.7
| Community Care - Clinical |  | 147.5 | 11% | 35% | 5% | 222.725 | [6 empty] | % variation | 0.1846%
| Secondary Shift - Clinical |  | 99.8 | 11% | 35% | 5% | 150.698
| Diagnostics - Clinical |  | 105.5 | 11% | 35% | 5% | 159.305
| Community, Secondary & Diagnostics - Shared Clinical |  | 113 | 11% | 35% | 5% | 170.63
| Clinical and Non-clinical Support |  | 108 | 11% | 25% | 5% | 152.28
| Staff Support |  | 302.2 | 11% | 25% | 5% | 426.102
Community Mental Health & Minor Injuries/Walk-in | Community Mental Health - Public |  | 65 | 11% | 25% | 5% | 91.65
| Minor Injuries - Public |  | 46.5 | 11% | 25% | 5% | 65.565
| Community Mental Health - Clinical |  | 106.5 | 11% | 35% | 5% | 160.815
| Minor Injuries - Clinical |  | 154 | 11% | 35% | 5% | 232.54
| Clinical and Non-clinical Support |  | 82 | 11% | 35% | 5% | 123.82
| Staff Support |  | 134.3 | 11% | 25% | 5% | 189.363
FM Hub | Non-clinical support |  | 48 | 11% | 25% | 5% | 67.68
[6 empty] | Subtotal | 4574.4785
Building uplifts |  |  |  |  | Communication | 12% | 548.9374
[5 empty] | Plant | 23% | 1052.1301
[6 empty] | Total GIA | 6175.546

## 1a) Unintegrated - Core
1a) Unintegrated - Core Services
Core functional content driven by the modelling
Typology | Service | Zone | Room name | Quantity | Size (m2) | Total size (m2) | Comments
Main Entrance
Core | Main Entrance | Public | Lobby: Main Entrance (Small) | 1 | 6 | 6
| Main Entrance | Public | External canopy shelter: Mobility scooter/pram (Small) | 0 | 8 | 0 | External
| Main Entrance | Public | Changing places | 1 | 12 | 12
| Main Entrance | Public | Nappy change room | 1 | 5 | 5
| Main Entrance | Public | Infant feeding room | 1 | 5.5 | 5.5
| Main Entrance | Public | Multi-faith room | 0 | 8 | 0 | May be provided depending on local requirements.
| Main Entrance | Public | Patient information/resource centre | 1 | 16 | 16
| Main Entrance | Public | Store: 10m2 | 1 | 10 | 10 | Third sector storage
| Main Entrance | Public | WC: Accessible | 1 | 4.5 | 4.5 | Visitor WC
[5 empty] | Subtotal | 59
General Practice (GP) Services
Core | General Practice (GP) Services | Public | Waiting area allowance: Per person | 78 | 2 | 156 | Assumes 2 x people waiting per clinical room, and 8 x people waiting for group rooms.
| General Practice (GP) Services | Public | Waiting area allowance: Child/play area: Per person | 8 | 2 | 16 | Assumes 10% allowance for child/play area, or a minimum of 6m2, whichever is larger.
| General Practice (GP) Services | Public | Reception: Per person | 3 | 5.5 | 16.5 | Assumes 1 x reception space per 35 people.
| General Practice (GP) Services | Public | Self-check-in kiosk | 3 | 2.5 | 7.5 | Assumes 1 x self-check-in per 35 people.
| General Practice (GP) Services | Public | WC: Semi-ambulant | 4 | 2.5 | 10 | Includes specimen WCs.
| General Practice (GP) Services | Public | WC: Accessible | 2 | 4.5 | 9 | Includes specimen WCs.
| General Practice (GP) Services | Public | Interview/quiet room (Small) | 2 | 8 | 16
[5 empty] | Subtotal | 231
Core | General Practice (GP) Services | Clinical zone | Consulting/examination room: Two-sided couch access | 16 | 13.5 | 216
| General Practice (GP) Services | Clinical zone | Consultation/treatment room: Three-sided couch access | 4 | 16 | 64
| General Practice (GP) Services | Clinical zone | Treatment room (Standard) | 4 | 16 | 64 | Assume standard treatment room suffices.
| General Practice (GP) Services | Clinical zone | Treatment room (Bariatric) | 1 | 20 | 20
| General Practice (GP) Services | Clinical zone | Group room | 3 | 32.5 | 97.5 | Can be used flexibly as a seminar / MDT room
| General Practice (GP) Services | Clinical zone | Store: 5m2 | 1.5 | 5 | 7.5 | Group room storage (assume majority of equipment etc. stored in the room)
| General Practice (GP) Services | Clinical zone | Pantry/refreshment area | 1 | 8 | 8 | Where more than 2 group rooms are provided
| General Practice (GP) Services | Clinical zone | Specimen WC: Independent wheelchair | 2 | 4.5 | 9
[5 empty] | Subtotal | 486
Core | General Practice (GP) Services | Clinical and non-clinical support zone | Clean utility (Small) | 2 | 8 | 16 | 1 per 12 C/E rooms or 1 per 4 treatment rooms
| General Practice (GP) Services | Clinical and non-clinical support zone | Dirty utility (Small) | 2 | 8 | 16 | 1 per 12 C/E rooms or 1 per 4 treatment rooms
| General Practice (GP) Services | Clinical and non-clinical support zone | Near patient testing room | 1 | 8 | 8
| General Practice (GP) Services | Clinical and non-clinical support zone | Bay: Resus trolley | 1 | 2 | 2
| General Practice (GP) Services | Clinical and non-clinical support zone | Store: 8m2 | 1 | 8 | 8 | Clinical supplies
| General Practice (GP) Services | Clinical and non-clinical support zone | Store: Ready to use gas cylinders | 1 | 2 | 2
| General Practice (GP) Services | Clinical and non-clinical support zone | Store: 10m2 | 1 | 10 | 10 | General/equipment store
| General Practice (GP) Services | Clinical and non-clinical support zone | Cleaner's room | 1 | 8 | 8
| General Practice (GP) Services | Clinical and non-clinical support zone | Disposal hold (Small) | 1 | 2 | 2
[5 empty] | Subtotal | 72
Core | General Practice (GP) Services | Hot zone | Staff shower/change: Gender neutral: Accessible | 1 | 4.5 | 4.5
| General Practice (GP) Services | Hot zone | Sluice | 1 | 6 | 6
| General Practice (GP) Services | Hot zone | Lobby: Entrance (small) | 1 | 4 | 4
| General Practice (GP) Services | Hot zone | Waiting area allowance: Per person | 6 | 2 | 12
[5 empty] | Subtotal | 26.5
Core | General Practice (GP) Services | Staff zone | Virtual consultation pod | 3 | 4.6 | 13.8 | Modelled outputs = 5, assume 70% carried out within dedicated booths, 30% carried out within quiet room
| General Practice (GP) Services | Staff zone | Interview/quiet room (Small) | 1 | 8 | 8
| General Practice (GP) Services | Staff zone | Office: 1 person | 3 | 8 | 24 | Practice managers
| General Practice (GP) Services | Staff zone | Hot desk area: Per desk | 18 | 5 | 90 | Assumes 0.6 x hot desks per clinical room with 40% carried out within clinical rooms (reflecting 60% room utilisation). Rounded to nearest whole number.
| General Practice (GP) Services | Staff zone | Personal/team storage: Per person | 18 | 0.125 | 2.25
| General Practice (GP) Services | Staff zone | Staff WC: Ambulant | 2 | 2 | 4 | Staff may also use specimen WCs.
| General Practice (GP) Services | Staff zone | Staff WC: Accessible | 1 | 4.5 | 4.5 | Staff may also use specimen WCs.
| General Practice (GP) Services | Staff zone | Staff rest and mini kitchen: Per person | 30 | 1.8 | 54 | Assume 1 place per generic clinical room.
| General Practice (GP) Services | Staff zone | Staff changing/shower/lockers: Per person | 30 | 1.4 | 42 | Assume 1 place per generic clinical room.
| General Practice (GP) Services | Staff zone | Staff shower: Accessible | 1 | 6 | 6
| General Practice (GP) Services | Staff zone | Staff shower/change: Gender neutral: Accessible | 1 | 4.5 | 4.5
| General Practice (GP) Services | Staff zone | Staff lockers: Per person | 5 | 0.5 | 2.5
[5 empty] | Subtotal | 255.55
|  |  |  | Subtotal - GP Services |  | 1071.05
Community Care and Secondary Shift Clinics
Core | Community Care and Secondary Shift Clinics | Public | Waiting area allowance: Per person | 50 | 2 | 100 | Assumes 2 x people waiting per clinical room, and 8 x people waiting for group rooms.
| Community Care and Secondary Shift Clinics | Public | Waiting area allowance: Child/play area: Per person | 5 | 2 | 10 | Assumes 10% allowance for child/play area, or a minimum of 6m2, whichever is larger.
| Community Care and Secondary Shift Clinics | Public | Reception: Per person | 2 | 5.5 | 11 | Assumes 1 x reception space per 35 people.
| Community Care and Secondary Shift Clinics | Public | Self-check-in kiosk | 2 | 2.5 | 5 | Assumes 1 x self check-in per 35 people.
| Community Care and Secondary Shift Clinics | Public | WC: Semi-ambulant | 2 | 2.5 | 5
| Community Care and Secondary Shift Clinics | Public | WC: Accessible | 1 | 4.5 | 4.5
| Community Care and Secondary Shift Clinics | Public | Interview/quiet room (Small) | 2 | 8 | 16
[5 empty] | Subtotal | 151.5
Core | Community Care Cluster | Clinical zone | Consulting/examination room: Two-sided couch access | 2 | 13.5 | 27
| Community Care Cluster | Clinical zone | Consultation/treatment room: Three-sided couch access | 1 | 16 | 16
| Community Care Cluster | Clinical zone | Treatment room (Standard) | 4 | 16 | 64
| Community Care Cluster | Clinical zone | Treatment room (Bariatric) | 1 | 20 | 20
| Community Care Cluster | Clinical zone | Specimen WC: Independent wheelchair | 1 | 4.5 | 4.5
| Community Care Cluster | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Clinical Supplies.
| Community Care Cluster | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Equipment.
[5 empty] | Subtotal | 147.5
Core | Secondary Shift Clinics Cluster | Clinical zone | Treatment room (Standard) | 2 | 16 | 32 | 60% of required Treatment room provision.
| Secondary Shift Clinics Cluster | Clinical zone | Treatment room (Bariatric) | 1 | 20 | 20 | 40% of required Treatment room provision. Bariatric provision.
| Secondary Shift Clinics Cluster | Clinical zone | WC: Accessible | 1 | 4.5 | 4.5 | e.g. gynae patients
| Secondary Shift Clinics Cluster | Clinical zone | Patient change: Wheelchair accessible | 3 | 4.5 | 13.5 | 1 per Treatment room.
| Secondary Shift Clinics Cluster | Clinical zone | Recovery bay: Recliner/chair | 3 | 4.6 | 13.8 | 1 per Treatment room.
| Secondary Shift Clinics Cluster | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Clinical supplies.
| Secondary Shift Clinics Cluster | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Equipment.
[5 empty] | Subtotal | 99.8
Core | Community Care and Secondary Shift Clinics | Shared Clinical zone | Pantry/refreshment area | 1 | 8 | 8
| Community Care and Secondary Shift Clinics | Shared Clinical zone | Group room | 3 | 32.5 | 97.5 | Can be used flexibly as a seminar / MDT room.
| Community Care and Secondary Shift Clinics | Shared Clinical zone | Store: 5m2 | 1.5 | 5 | 7.5 | Group room storage (assume majority of equipment etc. stored in the room)
[5 empty] | Subtotal | 113
Core | Community Care and Secondary Shift Clinics | Clinical and non-clinical support zone | Clean utility (Small) | 2 | 8 | 16 | 1 per 12 C/E rooms or 1 per 4 treatment rooms
| Community Care and Secondary Shift Clinics | Clinical and non-clinical support zone | Dirty utility (Small) | 2 | 8 | 16 | 1 per 12 C/E rooms or 1 per 4 treatment rooms
| Community Care and Secondary Shift Clinics | Clinical and non-clinical support zone | Scrub bay | 2 | 4 | 8 | Shared, associated with treatment rooms. 1 per 4 treatment rooms.
| Community Care and Secondary Shift Clinics | Clinical and non-clinical support zone | Near patient testing room | 1 | 8 | 8
| Community Care and Secondary Shift Clinics | Clinical and non-clinical support zone | Bay: Resus trolley | 2 | 2 | 4
| Community Care and Secondary Shift Clinics | Clinical and non-clinical support zone | Store: Ready to use gas cylinders | 1 | 2 | 2
| Community Care and Secondary Shift Clinics | Clinical and non-clinical support zone | Store: 10m2 | 1 | 10 | 10 | Bulk/general store.
| Community Care and Secondary Shift Clinics | Clinical and non-clinical support zone | Cleaner's room | 1 | 8 | 8
| Community Care and Secondary Shift Clinics | Clinical and non-clinical support zone | Disposal hold (Small) | 1 | 2 | 2
[5 empty] | Subtotal | 74
Core | Community Care and Secondary Shift Clinics | Staff zone | Virtual consultation pod | 4 | 4.6 | 18.4 | Combined total for Community Care and Secondary Shift Clinics. Modelled outputs = 6, assume 70% carried out within booths, 30% carried out within quiet room.
| Community Care and Secondary Shift Clinics | Staff zone | Interview/quiet room (Small) | 1 | 8 | 8
| Community Care and Secondary Shift Clinics | Staff zone | Office: 1 person | 1 | 8 | 8 | Community Care team lead.
| Community Care and Secondary Shift Clinics | Staff zone | Office: 1 person | 1 | 8 | 8 | Secondary Shift Clinics team lead.
| Community Care and Secondary Shift Clinics | Staff zone | Hot desk area: Per desk | 12 | 5 | 60 | Assumes 0.8 x hot desks per clinical room with 20% carried out within clinical rooms (reflecting 80% room utilisation). Rounded to nearest whole number.
| Community Care and Secondary Shift Clinics | Staff zone | Personal/team storage: Per person | 12 | 0.125 | 1.5
| Community Care and Secondary Shift Clinics | Staff zone | Staff WC: Ambulant | 2 | 2 | 4 | Staff may also use specimen WCs.
| Community Care and Secondary Shift Clinics | Staff zone | Staff WC: Accessible | 1 | 4.5 | 4.5 | Staff may also use specimen WCs.
| Community Care and Secondary Shift Clinics | Staff zone | Staff rest and mini kitchen: Per person | 15 | 1.8 | 27 | Assume 1 place per generic clinical room. Combined allowance.
| Community Care and Secondary Shift Clinics | Staff zone | Staff changing/shower/lockers: Per person | 15 | 1.4 | 21 | Assume 1 place per generic clinical room. Combined allowance.
| Community Care and Secondary Shift Clinics | Staff zone | Staff shower: Accessible | 1 | 6 | 6
| Community Care and Secondary Shift Clinics | Staff zone | Staff shower/change: Gender neutral: Accessible | 1 | 4.5 | 4.5
| Community Care and Secondary Shift Clinics | Staff zone | Staff lockers: Per person | 3 | 0.5 | 1.5
[5 empty] | Subtotal | 172.4
|  |  | Subtotal - Community Care & Secondary Shift Clinics |  |  | 758.2
FM Hub
Core | FM Hub | Non-clinical support zone | Disposal hold: 1700 litres | 1 | 8 | 8 | Shared across building.
| FM Hub | Non-clinical support zone | IT server/comms room (Small) | 1 | 20 | 20
[5 empty] | Subtotal | 28
[5 empty] | Total | 1916.25

## 2a) Integrated - Core
2a) Integrated - Core Services
Core functional content driven by the modelling
Typology | Service | Zone | Room name | Quantity | Size (m2) | Total size (m2) | Comments
Main Entrance
Core | Main Entrance | Public | Lobby: Main Entrance (Medium) | 1 | 8 | 8
| Main Entrance | Public | External canopy shelter: Mobility scooter/pram (Medium) | 0 | 12 | 0 | External
| Main Entrance | Public | Changing places | 1 | 12 | 12
| Main Entrance | Public | Nappy change room | 1 | 5 | 5
| Main Entrance | Public | Infant feeding room | 1 | 5.5 | 5.5
| Main Entrance | Public | Multi-faith room | 0 | 8 | 0 | May be provided depending on local requirements.
| Main Entrance | Public | Waiting area allowance: Per person | 76 | 2 | 152
| Main Entrance | Public | Waiting area allowance: Child/play area: Per person | 8 | 2 | 16
| Main Entrance | Public | Reception: Per person | 3 | 5.5 | 16.5 | 1 per 35 waiting spaces.
| Main Entrance | Public | Self-check-in kiosk | 3 | 2.5 | 7.5 | 1 per 35 waiting spaces.
| Main Entrance | Public | WC: Semi-ambulant | 3 | 2.5 | 7.5
| Main Entrance | Public | WC: Accessible | 2 | 4.5 | 9
| Main Entrance | Public | Interview/quiet room (Small) | 2 | 8 | 16
| Main Entrance | Public | Patient information/resource centre | 1 | 16 | 16
| Main Entrance | Public | Store: 10m2 | 1 | 10 | 10 | Third sector storage
| Main Entrance | Public | Community pharmacy (allowance) | 0 | 150 | 0
[5 empty] | Subtotal | 281
Core | Clinical | Clinical zone | Interview/quiet room (Small) | 1 | 8 | 8
| Clinical | Clinical zone | Consulting/examination room: Two-sided couch access | 9 | 13.5 | 121.5 | 60% of required C/E room provision.
| Clinical | Clinical zone | Consultation/treatment room: Three-sided couch access | 3 | 16 | 48 | 40% of required C/E room provision.
| Clinical | Clinical zone | Treatment room (Standard) | 5 | 16 | 80 | 70% of required Treatment room provision.
| Clinical | Clinical zone | Treatment room (Bariatric) | 2 | 20 | 40 | Bariatric
| Clinical | Clinical zone | Group room | 4 | 32.5 | 130 | Can be used flexibly as a seminar / MDT room
| Clinical | Clinical zone | Store: 5m2 | 4 | 5 | 20 | Group room storage
| Clinical | Clinical zone | Pantry/refreshment area | 1 | 8 | 8 | Where more than 2 group rooms are provided.
| Clinical | Clinical zone | Bay: Beverage | 1 | 3 | 3
| Clinical | Clinical zone | Specimen WC: Independent wheelchair | 3 | 4.5 | 13.5
| Clinical | Clinical zone | Patient change: Wheelchair accessible | 1 | 4.5 | 4.5
| Clinical | Clinical zone | Patient change: Ambulant | 1 | 3 | 3
| Clinical | Clinical zone | Recovery bay: Recliner/chair | 2 | 4.6 | 9.2 | 30% provision for treatment rooms.
| Clinical | Clinical zone | Scrub bay | 2 | 4 | 8 | Associated with treatment rooms. ~ 1 per 4
[5 empty] | Subtotal | 496.7
Core | Clinical and non-clinical support | Clinical and non-clinical support zone | Clean utility (Small) | 2 | 8 | 16 | 1 per 4 treatment rooms
| Clinical and non-clinical support | Clinical and non-clinical support zone | Dirty utility (Small) | 2 | 8 | 16 | 1 per 4 treatment rooms
| Clinical and non-clinical support | Clinical and non-clinical support zone | Near patient testing room | 1 | 8 | 8
| Clinical and non-clinical support | Clinical and non-clinical support zone | Bay: Resus trolley | 2 | 2 | 4
| Clinical and non-clinical support | Clinical and non-clinical support zone | Specimen reception | 2 | 4 | 8
| Clinical and non-clinical support | Clinical and non-clinical support zone | Store: 8m2 | 2 | 8 | 16 | Clinical supplies
| Clinical and non-clinical support | Clinical and non-clinical support zone | Store: Ready to use gas cylinders | 1 | 2 | 2
| Clinical and non-clinical support | Clinical and non-clinical support zone | Store: 15m2 | 1 | 15 | 15 | General store
| Clinical and non-clinical support | Clinical and non-clinical support zone | Store: 10m2 | 1 | 10 | 10 | Equipment
| Clinical and non-clinical support | Clinical and non-clinical support zone | Disposal hold (Small) | 2 | 2 | 4 | Assumes 1 per floor.
| Clinical and non-clinical support | Clinical and non-clinical support zone | Disposal hold: 1700 litres | 1 | 8 | 8
| Clinical and non-clinical support | Clinical and non-clinical support zone | Cleaner's room | 2 | 8 | 16 | Assumes 1 per floor.
| Clinical and non-clinical support | Clinical and non-clinical support zone | IT server/comms room (Small) | 1 | 10 | 10
[5 empty] | Subtotal | 133
Core | Hot zone | Hot zone | Staff shower/change: Gender neutral: Accessible | 1 | 4.5 | 4.5
| Hot zone | Hot zone | Sluice | 1 | 6 | 6
| Hot zone | Hot zone | Lobby: Entrance (small) | 1 | 4 | 4
| Hot zone | Hot zone | Waiting area allowance: Per person | 6 | 2 | 12
[5 empty] | Subtotal | 26.5
Core | Staff zone | Staff zone | Virtual consultation pod | 4 | 4.6 | 18.4 | Modelled outputs = 6, Assume 70% carried out within booths, 30% within quiet rooms
| Staff zone | Staff zone | Office: 2 people | 1 | 12 | 12 | Community care/secondary shift
| Staff zone | Staff zone | Office: 1 Person | 3 | 8 | 24 | GP Practice managers
| Staff zone | Staff zone | Shared workspace | 13 | 8.3 | 107.9 | Assumes ~ 0.5 x admin space (hotdesk) per generic clinical room; 20% to be carried out within clinical rooms. 3 x located on ground floor
| Staff zone | Staff zone | Personal/team storage: Per person | - | 0.125 |  | 1 x provided per workspace (13) included in above overall shared workspace allowance
| Staff zone | Staff zone | Photocopy/storage | - | 6 |  | 1 x included in above overall shared workspace allowance
| Staff zone | Staff zone | Interview/quiet room (Small) | - | 8 |  | 2 x included in above overall shared workspace allowance
| Staff zone | Staff zone | Quiet room | - | 6 |  | 2 x included in above overall shared workspace allowance
| Staff zone | Staff zone | Collaborative spaces | - | 0.75 |  | 1 x provided per workspace (13) included in above overall shared workspace allowance
| Staff zone | Staff zone | Clinical touchdown: Per person | 5 | 3 | 15 | Assumes 0.2 additional allowance per clinical room, rounded to nearest whole number.
| Staff zone | Staff zone | Staff WC: Ambulant | 6 | 2 | 12 | 5nr Staff WCs total required for 60nr staff under BS 6465. (7nr if in individual self-contained cubicles)
| Staff zone | Staff zone | Staff WC: Accessible | 1 | 4.5 | 4.5
| Staff zone | Staff zone | Staff rest: Ambulant dining/seating | 21 | 1.5 | 31.5 | Assumes 60 clinical staff, and provides accommodation for 40% occupation = 24 total (3 x wheelchair places)
| Staff zone | Staff zone | Staff rest: Wheelchair places | 3 | 3 | 9
| Staff zone | Staff zone | Staff kitchen | 1 | 12 | 12
| Staff zone | Staff zone | Staff lockers: Per person | 6 | 0.5 | 3 | Lockers BREEAM TRA 03 - 1nr locker per 10 staff.
| Staff zone | Staff zone | Staff shower/change: Gender neutral: Accessible | 1 | 4.5 | 4.5
| Staff zone | Staff zone | Staff changing/shower/lockers: Per person | 26 | 1.4 | 36.4 | Assumes 1 space per generic clinical room. To include for BREEAM Green Travel provisions - male and female change with individual private cubicle in each and separate change
[5 empty] | Subtotal | 290.2
[5 empty] | Total | 1227.4

## 1b) Unintegrated - Core +
1b) Unintegrated - Core+ Services
Core functional content driven by the modelling
Typology | Service | Zone | Room name | Quantity | Size (m2) | Total size (m2) | Comments
Main Entrance
Core+ | Main Entrance / Neighbourhood Support | Public | Lobby: Main Entrance (Medium) | 1 | 8 | 8
| Main Entrance / Neighbourhood Support | Public | External canopy shelter: Mobility scooter/pram (Medium) | 0 | 12 | 0 | External.
| Main Entrance / Neighbourhood Support | Public | Waiting area allowance: Per person | 4 | 2 | 8 | Assumes 1 per generic clinical space. Comfortable seating.
| Main Entrance / Neighbourhood Support | Public | Waiting area allowance: Child/play area: Per person | 3 | 2 | 6 | Assumes 10% allowance for child/play area, or a minimum of 6m2, whichever is larger.
| Main Entrance / Neighbourhood Support | Public | Reception: Per person | 1 | 5.5 | 5.5 | 1 per 35 people. Could also act as general help point/wayfinding for the building.
| Main Entrance / Neighbourhood Support | Public | Nappy change room | 1 | 5 | 5
| Main Entrance / Neighbourhood Support | Public | Infant feeding room | 1 | 5.5 | 5.5
| Main Entrance / Neighbourhood Support | Public | Changing places | 1 | 12 | 12
| Main Entrance / Neighbourhood Support | Public | Multi-faith room | 1 | 8 | 8
| Main Entrance / Neighbourhood Support | Public | WC: Accessible | 1 | 4.5 | 4.5
| Main Entrance / Neighbourhood Support | Public | WC: Semi-ambulant | 1 | 2.5 | 2.5
| Main Entrance / Neighbourhood Support | Public | Patient information/resource centre | 1 | 16 | 16 | The space may contain a mixture of tables, chairs, computer workstations and bookshelves. Display or leaflet stands or shelves may be provided. The size of the area will depend on the number/type of users, range of display information, whether the area is staffed or not, and whether it is an enclosed space or open bay. A suggestion for sizing the space would be 16 m2. This space will be used by: • 1–2 patients • 1 staff member (if resourced) • 1–2 others
| Main Entrance / Neighbourhood Support | Public | Store: 15m2 | 1 | 15 | 15 | Third sector storage
| Main Entrance / Neighbourhood Support | Public | Interview/quiet room (Small) | 2 | 8 | 16
[5 empty] | Subtotal | 112
Core+ | Main Entrance / Neighbourhood Support | Staff | Interview/quiet room (Small) | 1 | 8 | 8 | May be used for staff 1-to-1 and virtual consultations
| Main Entrance / Neighbourhood Support | Staff | Virtual consultation pod | 3 | 4.6 | 13.8 | Virtual consultation rationalised. Modelled outputs = 5. Assume 70% carried out within dedicated pod, 30% carried out within quiet room.
| Main Entrance / Neighbourhood Support | Staff | Staff rest and mini kitchen: Per person | 4 | 1.8 | 7.2 | Small tea point/rest area for staff.
[5 empty] | Subtotal | 29
|  |  |  | Subtotal - Main entrance |  | 141
General Practice (GP) Services
Core | General Practice (GP) Services | Public | Waiting area allowance: Per person | 78 | 2 | 156 | Assumes 2 x people waiting per clinical room, and 8 x people waiting for group rooms.
| General Practice (GP) Services | Public | Waiting area allowance: Child/play area: Per person | 8 | 2 | 16 | Assumes 10% allowance for child/play area, or a minimum of 6m2, whichever is larger.
| General Practice (GP) Services | Public | Reception: Per person | 3 | 5.5 | 16.5 | Assumes 1 x reception space per 35 people.
| General Practice (GP) Services | Public | Self-check-in kiosk | 3 | 2.5 | 7.5 | Assumes 1 x self-check-in per 35 people.
| General Practice (GP) Services | Public | WC: Semi-ambulant | 4 | 2.5 | 10 | Includes specimen WCs.
| General Practice (GP) Services | Public | WC: Accessible | 2 | 4.5 | 9 | Includes specimen WCs.
| General Practice (GP) Services | Public | Interview/quiet room (Small) | 2 | 8 | 16
[5 empty] | Subtotal | 231
Core | General Practice (GP) Services | Clinical zone | Consulting/examination room: Two-sided couch access | 16 | 13.5 | 216
| General Practice (GP) Services | Clinical zone | Consultation/treatment room: Three-sided couch access | 4 | 16 | 64
| General Practice (GP) Services | Clinical zone | Treatment room (Standard) | 4 | 16 | 64 | Assume standard treatment room suffices.
| General Practice (GP) Services | Clinical zone | Treatment room (Bariatric) | 1 | 20 | 20
| General Practice (GP) Services | Clinical zone | Group room | 3 | 32.5 | 97.5 | Can be used flexibly as a seminar / MDT room
| General Practice (GP) Services | Clinical zone | Store: 5m2 | 1.5 | 5 | 7.5 | Group room storage (assume majority of equipment etc. stored in the room)
| General Practice (GP) Services | Clinical zone | Pantry/refreshment area | 1 | 8 | 8 | Where more than 2 group rooms are provided
| General Practice (GP) Services | Clinical zone | Specimen WC: Independent wheelchair | 2 | 4.5 | 9
[5 empty] | Subtotal | 486
Core | General Practice (GP) Services | Clinical and non-clinical support zone | Clean utility (Small) | 2 | 8 | 16 | 1 per 12 C/E rooms or 1 per 4 treatment rooms
| General Practice (GP) Services | Clinical and non-clinical support zone | Dirty utility (Small) | 2 | 8 | 16 | 1 per 12 C/E rooms or 1 per 4 treatment rooms
| General Practice (GP) Services | Clinical and non-clinical support zone | Near patient testing room | 1 | 8 | 8
| General Practice (GP) Services | Clinical and non-clinical support zone | Bay: Resus trolley | 1 | 2 | 2
| General Practice (GP) Services | Clinical and non-clinical support zone | Store: 8m2 | 1 | 8 | 8 | Clinical supplies
| General Practice (GP) Services | Clinical and non-clinical support zone | Store: Ready to use gas cylinders | 1 | 2 | 2
| General Practice (GP) Services | Clinical and non-clinical support zone | Store: 10m2 | 1 | 10 | 10 | General/equipment store
| General Practice (GP) Services | Clinical and non-clinical support zone | Cleaner's room | 1 | 8 | 8
| General Practice (GP) Services | Clinical and non-clinical support zone | Disposal hold (Small) | 1 | 2 | 2
[5 empty] | Subtotal | 72
Core | General Practice (GP) Services | Hot zone | Staff shower/change: Gender neutral: Accessible | 1 | 4.5 | 4.5
| General Practice (GP) Services | Hot zone | Sluice | 1 | 6 | 6
| General Practice (GP) Services | Hot zone | Lobby: Entrance (small) | 1 | 4 | 4
| General Practice (GP) Services | Hot zone | Waiting area allowance: Per person | 6 | 2 | 12
[5 empty] | Subtotal | 26.5
Core | General Practice (GP) Services | Staff zone | Virtual consultation pod | 3 | 4.6 | 13.8 | Modelled outputs = 5, assume 70% carried out within dedicated booths, 30% carried out within quiet room
| General Practice (GP) Services | Staff zone | Interview/quiet room (Small) | 1 | 8 | 8
| General Practice (GP) Services | Staff zone | Office: 1 person | 3 | 8 | 24 | Practice managers
| General Practice (GP) Services | Staff zone | Hot desk area: Per desk | 18 | 5 | 90 | Assumes 0.6 x hot desks per clinical room with 40% carried out within clinical rooms (reflecting 60% room utilisation). Rounded to nearest whole number.
| General Practice (GP) Services | Staff zone | Personal/team storage: Per person | 18 | 0.125 | 2.25
| General Practice (GP) Services | Staff zone | Staff WC: Ambulant | 2 | 2 | 4 | Staff may also use specimen WCs.
| General Practice (GP) Services | Staff zone | Staff WC: Accessible | 1 | 4.5 | 4.5 | Staff may also use specimen WCs.
| General Practice (GP) Services | Staff zone | Staff rest and mini kitchen: Per person | 30 | 1.8 | 54 | Assume 1 place per generic clinical room.
| General Practice (GP) Services | Staff zone | Staff changing/shower/lockers: Per person | 30 | 1.4 | 42 | Assume 1 place per generic clinical room.
| General Practice (GP) Services | Staff zone | Staff shower: Accessible | 1 | 6 | 6
| General Practice (GP) Services | Staff zone | Staff shower/change: Gender neutral: Accessible | 1 | 4.5 | 4.5
| General Practice (GP) Services | Staff zone | Staff lockers: Per person | 5 | 0.5 | 2.5
[5 empty] | Subtotal | 255.55
|  |  |  | Subtotal - GP Services |  | 1071.05
Community Care, Secondary Shift Clinics and Family Hub
Core | Community Care and Secondary Shift Clinics | Public | Waiting area allowance: Per person | 50 | 2 | 100 | Assumes 2 x people waiting per clinical room, and 8 x people waiting for group rooms.
| Community Care and Secondary Shift Clinics | Public | Waiting area allowance: Child/play area: Per person | 5 | 2 | 10 | Assumes 10% allowance for child/play area, or a minimum of 6m2, whichever is larger.
| Community Care and Secondary Shift Clinics | Public | Reception: Per person | 2 | 5.5 | 11 | Assumes 1 x reception space per 35 people.
| Community Care and Secondary Shift Clinics | Public | Self-check-in kiosk | 2 | 2.5 | 5 | Assumes 1 x self check-in per 35 people.
| Community Care and Secondary Shift Clinics | Public | WC: Semi-ambulant | 3 | 2.5 | 7.5
| Community Care and Secondary Shift Clinics | Public | WC: Accessible | 2 | 4.5 | 9
| Community Care and Secondary Shift Clinics | Public | Interview/quiet room (Small) | 2 | 8 | 16
[5 empty] | Subtotal | 158.5
Core+ | Family Hubs | Public - Discrete zone | Waiting area allowance: Child/play area: Per person | 22 | 2 | 44 | Assumes 2 x people waiting per clinical room, and 8 x people waiting for group rooms.
| Family Hubs | Public - Discrete zone | Waiting area allowance: Child/play area: Per person | 7 | 2 | 14 | Assume 30% allowance for child/play area.
| Family Hubs | Public - Discrete zone | Reception: Per person | 1 | 5.5 | 5.5 | Assumes 1 x reception space per 35 people.
| Family Hubs | Public - Discrete zone | Self-check-in kiosk | 1 | 2.5 | 2.5 | Assumes 1 x self check-in per 35 people.
| Family Hubs | Public - Discrete zone | WC: Semi-ambulant | 1 | 2.5 | 2.5
| Family Hubs | Public - Discrete zone | WC: Accessible | 2 | 4.5 | 9
[5 empty] | Subtotal | 77.5
Core+ | Family Hubs | Clinical zone | Consulting/examination room: Two-sided couch access | 2 | 13.5 | 27
| Family Hubs | Clinical zone | Consultation/treatment room: Three-sided couch access | 1 | 16 | 16
| Family Hubs | Clinical zone | Group room | 2 | 32.5 | 65
| Family Hubs | Clinical zone | Store: 5m2 | 1 | 5 | 5 | Group room storage (assume majority of equipment etc. stored in the room)
| Family Hubs | Clinical zone | Bay: Beverage | 1 | 3 | 3
| Family Hubs | Clinical zone | Specimen WC: Independent wheelchair | 1 | 4.5 | 4.5
| Family Hubs | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Clinical supplies
| Family Hubs | Clinical zone | Store: 8m2 | 1 | 8 | 8 | General store
[5 empty] | Subtotal | 136.5
Core | Community Care Cluster | Clinical zone | Consulting/examination room: Two-sided couch access | 2 | 13.5 | 27
| Community Care Cluster | Clinical zone | Consultation/treatment room: Three-sided couch access | 1 | 16 | 16
| Community Care Cluster | Clinical zone | Treatment room (Standard) | 4 | 16 | 64
| Community Care Cluster | Clinical zone | Treatment room (Bariatric) | 1 | 20 | 20
| Community Care Cluster | Clinical zone | Specimen WC: Independent wheelchair | 1 | 4.5 | 4.5
| Community Care Cluster | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Clinical Supplies.
| Community Care Cluster | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Equipment.
[5 empty] | Subtotal | 147.5
Core | Secondary Shift Clinics Cluster | Clinical zone | Treatment room (Standard) | 2 | 16 | 32 | 60% of required Treatment room provision.
| Secondary Shift Clinics Cluster | Clinical zone | Treatment room (Bariatric) | 1 | 20 | 20 | 40% of required Treatment room provision. Bariatric provision.
| Secondary Shift Clinics Cluster | Clinical zone | WC: Accessible | 1 | 4.5 | 4.5 | e.g. gynae patients
| Secondary Shift Clinics Cluster | Clinical zone | Patient change: Wheelchair accessible | 3 | 4.5 | 13.5 | 1 per Treatment room.
| Secondary Shift Clinics Cluster | Clinical zone | Recovery bay: Recliner/chair | 3 | 4.6 | 13.8 | 1 per Treatment room.
| Secondary Shift Clinics Cluster | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Clinical supplies.
| Secondary Shift Clinics Cluster | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Equipment.
[5 empty] | Subtotal | 99.8
Core | Community Care and Secondary Shift Clinics | Shared Clinical zone | Pantry/refreshment area | 1 | 8 | 8
| Community Care and Secondary Shift Clinics | Shared Clinical zone | Group room | 3 | 32.5 | 97.5 | Can be used flexibly as a seminar / MDT room.
| Community Care and Secondary Shift Clinics | Shared Clinical zone | Store: 5m2 | 1.5 | 5 | 7.5 | Group room storage (assume majority of equipment etc. stored in the room)
[5 empty] | Subtotal | 113
Core+ | Community Care, Secondary Shift Clinics & Family Hub | Clinical and non-clinical support zone | Clean utility (Small) | 2 | 8 | 16 | 1 per 12 C/E rooms or 1 per 4 treatment rooms
| Community Care, Secondary Shift Clinics & Family Hub | Clinical and non-clinical support zone | Dirty utility (Small) | 2 | 8 | 16 | 2 per 12 C/E rooms or 1 per 4 treatment rooms
| Community Care, Secondary Shift Clinics & Family Hub | Clinical and non-clinical support zone | Scrub bay | 2 | 4 | 8 | Shared, associated with treatment rooms. 1 per 4 treatment rooms.
| Community Care, Secondary Shift Clinics & Family Hub | Clinical and non-clinical support zone | Near patient testing room | 1 | 8 | 8
| Community Care, Secondary Shift Clinics & Family Hub | Clinical and non-clinical support zone | Bay: Resus trolley | 2 | 2 | 4
| Community Care, Secondary Shift Clinics & Family Hub | Clinical and non-clinical support zone | Store: Ready to use gas cylinders | 2 | 2 | 4
| Community Care, Secondary Shift Clinics & Family Hub | Clinical and non-clinical support zone | Store: 15m2 | 1 | 15 | 15 | Bulk/general store
| Community Care, Secondary Shift Clinics & Family Hub | Clinical and non-clinical support zone | Disposal hold (Small) | 1 | 2 | 2
| Community Care, Secondary Shift Clinics & Family Hub | Clinical and non-clinical support zone | Cleaner's room | 1 | 8 | 8
[5 empty] | Subtotal | 81
Core+ | Community Care, Secondary Shift Clinics & Family Hub | Staff zone | Virtual consultation pod | 6 | 4.6 | 27.6 | Total requirement for services = 8. Assume 70% carried out in dedicated booths, 30% carried out within quiet rooms.
| Community Care, Secondary Shift Clinics & Family Hub | Staff zone | Interview/quiet room (Small) | 2 | 8 | 16
| Community Care, Secondary Shift Clinics & Family Hub | Staff zone | Office: 1 person | 1 | 8 | 8 | Community Care team lead.
| Community Care, Secondary Shift Clinics & Family Hub | Staff zone | Office: 1 person | 1 | 8 | 8 | Secondary Shift Clinics team lead.
| Community Care, Secondary Shift Clinics & Family Hub | Staff zone | Office: 1 person | 1 | 8 | 8 | Family Hub lead.
| Community Care, Secondary Shift Clinics & Family Hub | Staff zone | Hot desk area: Per desk | 16.8 | 5 | 84 | General administration. Assumes 0.8 x hot desk per generic clinical room to reflect 80% room utilisation. Combined allowance.
| Community Care, Secondary Shift Clinics & Family Hub | Staff zone | Personal/team storage: Per person | 16.8 | 0.125 | 2.1
| Community Care, Secondary Shift Clinics & Family Hub | Staff zone | Staff WC: Ambulant | 3 | 2 | 6 | Staff may also use specimen WCs.
| Community Care, Secondary Shift Clinics & Family Hub | Staff zone | Staff WC: Accessible | 1 | 4.5 | 4.5 | Staff may also use specimen WCs.
| Community Care, Secondary Shift Clinics & Family Hub | Staff zone | Staff rest and mini kitchen: Per person | 21 | 1.8 | 37.8 | Assume 1 place per generic clinical room. Combined allowance.
| Community Care, Secondary Shift Clinics & Family Hub | Staff zone | Staff changing/shower/lockers: Per person | 21 | 1.4 | 29.4 | Assume 1 place per generic clinical room. Combined allowance.
| Community Care, Secondary Shift Clinics & Family Hub | Staff zone | Staff shower: Accessible | 1 | 6 | 6
| Community Care, Secondary Shift Clinics & Family Hub | Staff zone | Staff shower/change: Gender neutral: Accessible | 1 | 4.5 | 4.5
| Community Care, Secondary Shift Clinics & Family Hub | Staff zone | Staff lockers: Per person | 7 | 0.5 | 3.5
[5 empty] | Subtotal | 245.4
|  |  | Subtotal - Community Care, Secondary Shift Clinics & Family Hub |  |  | 1059.2
Community Mental Health & Minor Injuries/Walk-ins
Core+ | Community Mental Health | Public - Discrete zone | Lobby: Main Entrance (Small) | 1 | 6 | 6
| Community Mental Health | Public - Discrete zone | Waiting area allowance: Per person | 14 | 2 | 28 | Assumes 2 x people waiting per clinical room, and 8 x people waiting for group rooms. Separation of adult / child mental health services required (if provided)
| Community Mental Health | Public - Discrete zone | Waiting area allowance: Child/play area: Per person | 3 | 2 | 6 | Assume 10% allowance for child/play area or minimum 6m2, whichever is larger. Separation of adult / child mental health services required (if provided)
| Community Mental Health | Public - Discrete zone | Reception: Per person | 1 | 5.5 | 5.5 | 1 per 35 people.
| Community Mental Health | Public - Discrete zone | WC: Semi-ambulant | 2 | 2.5 | 5 | Anti-ligature.
| Community Mental Health | Public - Discrete zone | WC: Accessible | 1 | 4.5 | 4.5 | Anti-ligature.
| Community Mental Health | Public - Discrete zone | Multisensory room | 1 | 10 | 10
[5 empty] | Subtotal | 65
Core+ | Minor Injuries / Walk-in | Public | Waiting area allowance: Per person | 14 | 2 | 28 | Assumes 2 per generic clinical space (incl. plaster room).
| Minor Injuries / Walk-in | Public | Waiting area allowance: Child/play area: Per person | 3 | 2 | 6 | Assume 10% allowance for child/play area or minimum 6m2, whichever is larger.
| Minor Injuries / Walk-in | Public | Reception: Per person | 1 | 5.5 | 5.5 | 1 per 35 people.
| Minor Injuries / Walk-in | Public | WC: Semi-ambulant | 1 | 2.5 | 2.5
| Minor Injuries / Walk-in | Public | WC: Accessible | 1 | 4.5 | 4.5
[5 empty] | Subtotal | 46.5
Core+ | Community Mental Health | Clinical zone | Interview/quiet room (Small) | 1 | 8 | 8
| Community Mental Health | Clinical zone | Consulting/examination room: Two-sided couch access | 1 | 13.5 | 13.5 | Assumes two-sided access is sufficient.
| Community Mental Health | Clinical zone | Group room | 1 | 32.5 | 32.5
| Community Mental Health | Clinical zone | Treatment room (Standard) | 1 | 16 | 16
| Community Mental Health | Clinical zone | Store: 5m2 | 1 | 5 | 5 | Group room storage.
| Community Mental Health | Clinical zone | Observation room | 1 | 8 | 8 | Adjacent to group room
| Community Mental Health | Clinical zone | Bay: Beverage | 1 | 3 | 3
| Community Mental Health | Clinical zone | WC: Accessible | 1 | 4.5 | 4.5 | Anti-ligature
| Community Mental Health | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Equipment/general store
| Community Mental Health | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Clinical supplies
[5 empty] | Subtotal | 106.5
Core+ | Minor Injuries / Walk-in | Clinical zone | Consulting/examination room: Two-sided couch access | 1 | 13.5 | 13.5
| Minor Injuries / Walk-in | Clinical zone | Consultation/treatment room: Three-sided couch access | 1 | 16 | 16
| Minor Injuries / Walk-in | Clinical zone | Treatment room (Standard) | 4 | 16 | 64
| Minor Injuries / Walk-in | Clinical zone | Treatment room (Bariatric) | 1 | 20 | 20
| Minor Injuries / Walk-in | Clinical zone | Plaster room | 1 | 16 | 16
| Minor Injuries / Walk-in | Clinical zone | Store: Plaster room | 1 | 4 | 4
| Minor Injuries / Walk-in | Clinical zone | Specimen WC: Independent Wheelchair | 1 | 4.5 | 4.5
| Minor Injuries / Walk-in | Clinical and non-clinical support zone | Store: 8m2 | 1 | 8 | 8 | Clinical supplies
| Minor Injuries / Walk-in | Clinical and non-clinical support zone | Store: 8m2 | 1 | 8 | 8 | Equipment
[5 empty] | Subtotal | 154
Core+ | Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Bay: Resus trolley | 1 | 2 | 2
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Bay: Mobile imaging | 1 | 3 | 3 | Make accessible
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Clean utility (Small) | 2 | 8 | 16 | 1 per 12 C/E rooms or 1 per 4 treatment rooms
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Dirty utility (Small) | 2 | 8 | 16 | 1 per 12 C/E rooms or 1 per 4 treatment rooms
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Near patient testing room | 1 | 8 | 8
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Medicine store/preparation room | 1 | 12 | 12
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Bay: Linen trolley | 1 | 3 | 3
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Store: ready to use gas cylinders | 1 | 2 | 2
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Store: 10m2 | 1 | 10 | 10 | General/bulk store
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Disposal hold (Small) | 1 | 2 | 2
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Cleaner's room | 1 | 8 | 8
[5 empty] | Subtotal | 82
Core+ | Community Mental Health & Minor Injuries / Walk-in | Staff zone | Virtual consultation pod | 2 | 4.6 | 9.2 | Combined allowance.
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Office: 1 person | 1 | 8 | 8 | CMH Team lead
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Office: 1 person | 1 | 8 | 8 | Minor Injuries Team lead
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Hot desk area: Per desk | 9.6 | 5 | 48 | Assumes 0.8 x per generic clinical space incl. plaster room
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Personal/team storage: Per person | 9.6 | 0.125 | 1.2
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Staff WC: Ambulant | 2 | 2 | 4
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Staff WC: Accessible | 1 | 4.5 | 4.5
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Staff rest and mini kitchen: Per person | 12 | 1.8 | 21.6 | Assumes ~ 1 per generic clinical space.
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Staff changing/shower/lockers: Per person | 12 | 1.4 | 16.8 | Assumes 1 per generic clinical space.
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Staff shower: Accessible | 1 | 6 | 6
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Staff shower/change: Gender neutral: Accessible | 1 | 4.5 | 4.5
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Staff lockers: Per person | 5 | 0.5 | 2.5
[5 empty] | Subtotal | 134.3
|  |  | Subtotal - Community Mental Health & Minor Injuries / Walk-in |  |  | 588.3
FM Hub
Core+ | FM Hub | Non-clinical support zone | Disposal hold: 1700 litres | 1 | 8 | 8 | Shared across building.
| FM Hub | Non-clinical support zone | IT server/comms room (Medium) | 1 | 30 | 30
[5 empty] | Subtotal | 38
[5 empty] | Total | 2897.55

## 2b) Integrated - Core +
2b) Integrated - Core+ Services
Core functional content driven by the modelling
Typology | Service | Zone | Room name | Quantity | Size (m2) | Total size (m2) | Comments
Main Entrance
Core+ | Main Entrance | Public | Lobby: Main Entrance (Medium) | 1 | 8 | 8
| Main Entrance | Public | External canopy shelter: Mobility scooter/pram (Medium) | 0 | 12 | 0 | External.
| Main Entrance | Public | Changing places | 1 | 12 | 12
| Main Entrance | Public | Nappy change room | 1 | 5 | 5
| Main Entrance | Public | Infant feeding room | 1 | 5.5 | 5.5
| Main Entrance | Public | Multi-faith room | 1 | 8 | 8
| Main Entrance | Public | Waiting area allowance: Per person | 112 | 2 | 224 | Assume 2 people per generic clinical space amd 8 people per group room
| Main Entrance | Public | Waiting area allowance: Child/play area: Per person | 12 | 2 | 24 | Assume 10% of waiting for childrens/play area
| Main Entrance | Public | Reception: Per person | 3 | 5.5 | 16.5 | 1 per 35 people
| Main Entrance | Public | Self-check-in kiosk | 3 | 2.5 | 7.5 | 1 per 35 people
| Main Entrance | Public | WC: Semi-ambulant | 3 | 2.5 | 7.5 | Total WC allowance includes specimen/accessible WCs within clinical zone. 8nr patient WCs total required to meeting BS6465-1,
| Main Entrance | Public | WC: Accessible | 2 | 4.5 | 9 | Total WC allowance includes specimen/accessible WCs within clinical zone.
| Main Entrance | Public | Patient information/resource centre | 1 | 16 | 16
| Main Entrance | Public | Interview/quiet room (Small) | 3 | 8 | 24
| Main Entrance | Public | Store: 15m2 | 1 | 15 | 15 | Third sector storage.
| Main Entrance | Public - Mental Health | Lobby: Main Entrance (Small) | 1 | 6 | 6
| Main Entrance | Public - Mental Health | Waiting area allowance: Per person | 7 | 2 | 14
| Main Entrance | Public - Mental Health | Waiting area allowance: Child/play area: Per person | 3 | 2 | 6
| Main Entrance | Public - Mental Health | Reception: Per person | 1 | 5.5 | 5.5
| Main Entrance | Public - Mental Health | WC: Accessible | 1 | 4.5 | 4.5 | Anti ligature
| Main Entrance | Public - Mental Health | Multisensory room | 1 | 10 | 10
| Main Entrance | Public | Community pharmacy (allowance) | 0 | 150 | 0
[5 empty] | Subtotal | 428
Core+ | Clinical | Clinical zone | Interview/quiet room (Small) | 2 | 8 | 16
| Clinical | Clinical zone | Consulting/examination room: Two-sided couch access | 13 | 13.5 | 175.5
| Clinical | Clinical zone | Consultation/treatment room: Three-sided couch access | 3 | 16 | 48
| Clinical | Clinical zone | Treatment room (Standard) | 9 | 16 | 144
| Clinical | Clinical zone | Treatment room (Bariatric) | 2 | 20 | 40
| Clinical | Clinical zone | Group room | 6 | 32.5 | 195 | Can be used flexibly as a seminar / MDT room
| Clinical | Clinical zone | Store: 5m2 | 6 | 5 | 30 | Group room storage
| Clinical | Clinical zone | Observation room | 1 | 8 | 8 | Mental health - adjoined to group room
| Clinical | Clinical zone | Specimen WC: Independent wheelchair | 3 | 4.5 | 13.5
| Clinical | Clinical zone | Patient change: Wheelchair accessible | 2 | 4.5 | 9 | Assume 30% of treatment room activity
| Clinical | Clinical zone | Patient change: Ambulant | 1 | 3 | 3
| Clinical | Clinical zone | Recovery bay: Recliner/chair | 3 | 4.6 | 13.8 | Assume 30% of treatment room activity
| Clinical | Clinical zone | WC: Accessible | 1 | 4.5 | 4.5 | Anti-ligature - Mental health
| Clinical | Clinical zone | Pantry/refreshment area | 1 | 8 | 8 | Where more than 2 group rooms are provided.
| Clinical | Clinical zone | Bay: Beverage | 2 | 3 | 6
| Clinical | Clinical zone | Scrub bay | 3 | 4 | 12 | Associated with treatment rooms, ~ 1 per 4
[5 empty] | Subtotal | 726.3
Core+ | Clinical and non-clinical support | Clinical and non-clinical support zone | Clean utility (Small) | 3 | 8 | 24 | 1 per 12 C/E rooms or 1 per 4 treatment rooms
| Clinical and non-clinical support | Clinical and non-clinical support zone | Dirty utility (Small) | 3 | 8 | 24 | 1 per 12 C/E rooms or 1 per 4 treatment rooms
| Clinical and non-clinical support | Clinical and non-clinical support zone | Near patient testing room | 1 | 8 | 8
| Clinical and non-clinical support | Clinical and non-clinical support zone | Medicine store/preparation room | 1 | 12 | 12
| Clinical and non-clinical support | Clinical and non-clinical support zone | Bay: Resus trolley | 2 | 2 | 4
| Clinical and non-clinical support | Clinical and non-clinical support zone | Bay: Mobile imaging | 2 | 3 | 6
| Clinical and non-clinical support | Clinical and non-clinical support zone | Bay: Linen trolley | 2 | 3 | 6
| Clinical and non-clinical support | Clinical and non-clinical support zone | Specimen reception | 2 | 4 | 8
| Clinical and non-clinical support | Clinical and non-clinical support zone | Store: 10m2 | 2 | 10 | 20 | Clinical supplies
| Clinical and non-clinical support | Clinical and non-clinical support zone | Store: Ready to use gas cylinders | 2 | 2 | 4
| Clinical and non-clinical support | Clinical and non-clinical support zone | Store: 20m2 | 1 | 20 | 20 | General store
| Clinical and non-clinical support | Clinical and non-clinical support zone | Store: 15m2 | 1 | 15 | 15 | Equipment
| Clinical and non-clinical support | Clinical and non-clinical support zone | Disposal hold (Small) | 2 | 2 | 4 | 1 per floor
| Clinical and non-clinical support | Clinical and non-clinical support zone | Disposal hold: 1700 litres | 1 | 8 | 8
| Clinical and non-clinical support | Clinical and non-clinical support zone | Cleaner's room | 2 | 8 | 16 | 1 per floor
| Clinical and non-clinical support | Clinical and non-clinical support zone | Plaster room | 1 | 16 | 16
| Clinical and non-clinical support | Clinical and non-clinical support zone | Store: Plaster room | 1 | 4 | 4
| Clinical and non-clinical support | Clinical and non-clinical support zone | IT server/comms room (Medium) | 1 | 30 | 30
[5 empty] | Subtotal | 229
Core+ | Hot zone | Hot zone | Staff shower/change: Gender neutral: Accessible | 1 | 4.5 | 4.5
| Hot zone | Hot zone | Sluice | 1 | 6 | 6
| Hot zone | Hot zone | Lobby: Entrance (small) | 1 | 4 | 4
| Hot zone | Hot zone | Waiting area allowance: Per person | 6 | 2 | 12
[5 empty] | Subtotal | 26.5
Core+ | Staff zone | Staff zone | Virtual consultation pod | 11 | 4.6 | 50.6 | Modelled output = 15; Assume 70% carried out within booths, 30% within quiet rooms
| Staff zone | Staff zone | Office: 2 people | 3 | 12 | 36 | Service managers / team leads
| Staff zone | Staff zone | Office: 1 person | 3 | 8 | 24 | GP Practice managers
| Staff zone | Staff zone | Shared workspace | 22 | 8.3 | 182.6 | Assumes ~ 0.6 admin space (hotdesk) per generic clinical room; 20% to be carried out within clinical rooms. 9 on ground floor
| Staff zone | Staff zone | Personal/team storage: Per person | - | 0.125 |  | 1 x provided per workspace (22) included in above overall shared workspace allowance
| Staff zone | Staff zone | Photocopy/storage | - | 6 |  | 1 x included in above overall shared workspace allowance
| Staff zone | Staff zone | Interview/quiet room (Small) | - | 8 |  | 3 x included in above overall shared workspace allowance
| Staff zone | Staff zone | Quiet room | - | 6 |  | 4 x included in above overall shared workspace allowance
| Staff zone | Staff zone | Collaborative spaces | - | 0.75 |  | 1 x provided per workspace (22) included in above overall shared workspace allowance
| Staff zone | Staff zone | Clinical touchdown: Per person | 8 | 3 | 24 | Assumes 0.2 additional allowance per clinical room, rounded to nearest whole number.
| Staff zone | Staff zone | Staff WC: Ambulant | 8 | 2 | 16 | 8nr Staff WCs total required to meet BS6465-1 for 98nr staff (10nr if in individual self-contained cubicles - 25% added for longer occupancy time to include handwashing)
| Staff zone | Staff zone | Staff WC: Accessible | 2 | 4.5 | 9
| Staff zone | Staff zone | Staff rest: Ambulant dining/seating | 36 | 1.5 | 54 | Assumes 98 staff, and provides accommodation for 40% occupation = 40 total (4 x wheelchair places)
| Staff zone | Staff zone | Staff rest: Wheelchair places | 4 | 3 | 12
| Staff zone | Staff zone | Staff kitchen | 1 | 12 | 12
| Staff zone | Staff zone | Staff lockers: Per person | 10 | 0.5 | 5 | Lockers BREEAM TRA 03 - 1nr locker per 10 staff.
| Staff zone | Staff zone | Staff shower/change: Gender neutral: Accessible | 1 | 4.5 | 4.5
| Staff zone | Staff zone | Staff changing/shower/lockers: Per person | 38 | 1.4 | 53.2 | Assumes 1 per generic clinical room
[5 empty] | Subtotal | 482.9
[5 empty] | Total | 1892.7

## 1c) Unintegrated - Core ++
1b) Unintegrated - Core++ Services
Core functional content driven by the modelling
Typology | Service | Zone | Room name | Quantity | Size (m2) | Total size (m2) | Comments
Main Entrance
Core+ | Main Entrance / Neighbourhood Support | Public | Lobby: Main Entrance (Medium) | 1 | 8 | 8
| Main Entrance / Neighbourhood Support | Public | External canopy shelter: Mobility scooter/pram (Medium) | 0 | 12 | 0 | External.
| Main Entrance / Neighbourhood Support | Public | Waiting area allowance: Per person | 7 | 2 | 14 | Assumes 1 per generic clinical space. Comfortable seating.
| Main Entrance / Neighbourhood Support | Public | Waiting area allowance: Child/play area: Per person | 3 | 2 | 6 | Assumes 10% allowance for child/play area, or a minimum of 6m2, whichever is larger.
| Main Entrance / Neighbourhood Support | Public | Reception: Per person | 1 | 5.5 | 5.5 | 1 per 35 people. Could also act as general help point/wayfinding for the building.
| Main Entrance / Neighbourhood Support | Public | Nappy change room | 1 | 5 | 5
| Main Entrance / Neighbourhood Support | Public | Infant feeding room | 1 | 5.5 | 5.5
| Main Entrance / Neighbourhood Support | Public | Changing places | 1 | 12 | 12
| Main Entrance / Neighbourhood Support | Public | Multi-faith room | 1 | 8 | 8
| Main Entrance / Neighbourhood Support | Public | WC: Accessible | 1 | 4.5 | 4.5
| Main Entrance / Neighbourhood Support | Public | WC: Semi-ambulant | 1 | 2.5 | 2.5
| Main Entrance / Neighbourhood Support | Public | Patient information/resource centre | 1 | 16 | 16 | The space may contain a mixture of tables, chairs, computer workstations and bookshelves. Display or leaflet stands or shelves may be provided. The size of the area will depend on the number/type of users, range of display information, whether the area is staffed or not, and whether it is an enclosed space or open bay. A suggestion for sizing the space would be 16 m2. This space will be used by: • 1–2 patients • 1 staff member (if resourced) • 1–2 others
| Main Entrance / Neighbourhood Support | Public | Store: 15m2 | 1 | 15 | 15 | Third sector storage
| Main Entrance / Neighbourhood Support | Public | Interview/quiet room (Small) | 2 | 8 | 16 | Reduced to 1 as people may receive support in the patient information/resource centre.
[5 empty] | Subtotal | 118
Core+ | Main Entrance / Neighbourhood Support | Staff | Interview/quiet room (Small) | 1 | 8 | 8 | May be used for staff 1-to-1 and virtual consultations
| Main Entrance / Neighbourhood Support | Staff | Virtual consultation pod | 3 | 4.6 | 13.8 | Virtual consultation rationalised. Modelled outputs = 5. Assume 70% carried out within dedicated pod, 30% carried out within quiet room.
| Main Entrance / Neighbourhood Support | Staff | Staff rest and mini kitchen: Per person | 4 | 1.8 | 7.2 | Small tea point/rest area for staff.
[5 empty] | Subtotal | 29
|  |  |  | Subtotal - Main entrance |  | 147
General Practice (GP) Services
Core | General Practice (GP) Services | Public | Waiting area allowance: Per person | 78 | 2 | 156 | Assumes 2 x people waiting per clinical room, and 8 x people waiting for group rooms.
| General Practice (GP) Services | Public | Waiting area allowance: Child/play area: Per person | 8 | 2 | 16 | Assumes 10% allowance for child/play area, or a minimum of 6m2, whichever is larger.
| General Practice (GP) Services | Public | Reception: Per person | 3 | 5.5 | 16.5 | Assumes 1 x reception space per 35 people.
| General Practice (GP) Services | Public | Self-check-in kiosk | 3 | 2.5 | 7.5 | Assumes 1 x self-check-in per 35 people.
| General Practice (GP) Services | Public | WC: Semi-ambulant | 4 | 2.5 | 10 | Includes specimen WCs.
| General Practice (GP) Services | Public | WC: Accessible | 2 | 4.5 | 9 | Includes specimen WCs.
| General Practice (GP) Services | Public | Interview/quiet room (Small) | 2 | 8 | 16
[5 empty] | Subtotal | 231
Core | General Practice (GP) Services | Clinical zone | Consulting/examination room: Two-sided couch access | 16 | 13.5 | 216
| General Practice (GP) Services | Clinical zone | Consultation/treatment room: Three-sided couch access | 4 | 16 | 64
| General Practice (GP) Services | Clinical zone | Treatment room (Standard) | 4 | 16 | 64 | Assume standard treatment room suffices.
| General Practice (GP) Services | Clinical zone | Treatment room (Bariatric) | 1 | 20 | 20
| General Practice (GP) Services | Clinical zone | Group room | 3 | 32.5 | 97.5 | Can be used flexibly as a seminar / MDT room
| General Practice (GP) Services | Clinical zone | Store: 5m2 | 1.5 | 5 | 7.5 | Group room storage (assume majority of equipment etc. stored in the room)
| General Practice (GP) Services | Clinical zone | Pantry/refreshment area | 1 | 8 | 8 | Where more than 2 group rooms are provided
| General Practice (GP) Services | Clinical zone | Specimen WC: Independent wheelchair | 2 | 4.5 | 9
[5 empty] | Subtotal | 486
Core | General Practice (GP) Services | Clinical and non-clinical support zone | Clean utility (Small) | 2 | 8 | 16 | 1 per 12 C/E rooms or 1 per 4 treatment rooms
| General Practice (GP) Services | Clinical and non-clinical support zone | Dirty utility (Small) | 2 | 8 | 16 | 1 per 12 C/E rooms or 1 per 4 treatment rooms
| General Practice (GP) Services | Clinical and non-clinical support zone | Near patient testing room | 1 | 8 | 8
| General Practice (GP) Services | Clinical and non-clinical support zone | Bay: Resus trolley | 1 | 2 | 2
| General Practice (GP) Services | Clinical and non-clinical support zone | Store: 8m2 | 1 | 8 | 8 | Clinical supplies
| General Practice (GP) Services | Clinical and non-clinical support zone | Store: Ready to use gas cylinders | 1 | 2 | 2
| General Practice (GP) Services | Clinical and non-clinical support zone | Store: 10m2 | 1 | 10 | 10 | General/equipment store
| General Practice (GP) Services | Clinical and non-clinical support zone | Cleaner's room | 1 | 8 | 8
| General Practice (GP) Services | Clinical and non-clinical support zone | Disposal hold (Small) | 1 | 2 | 2
[5 empty] | Subtotal | 72
Core | General Practice (GP) Services | Hot zone | Staff shower/change: Gender neutral: Accessible | 1 | 4.5 | 4.5
| General Practice (GP) Services | Hot zone | Sluice | 1 | 6 | 6
| General Practice (GP) Services | Hot zone | Lobby: Entrance (small) | 1 | 4 | 4
| General Practice (GP) Services | Hot zone | Waiting area allowance: Per person | 6 | 2 | 12
[5 empty] | Subtotal | 26.5
Core | General Practice (GP) Services | Staff zone | Virtual consultation pod | 3 | 4.6 | 13.8 | Modelled outputs = 5, assume 70% carried out within dedicated booths, 30% carried out within quiet room
| General Practice (GP) Services | Staff zone | Interview/quiet room (Small) | 1 | 8 | 8
| General Practice (GP) Services | Staff zone | Office: 1 person | 3 | 8 | 24 | Practice managers
| General Practice (GP) Services | Staff zone | Hot desk area: Per desk | 18 | 5 | 90 | Assumes 0.6 x hot desks per clinical room with 40% carried out within clinical rooms (reflecting 60% room utilisation). Rounded to nearest whole number.
| General Practice (GP) Services | Staff zone | Personal/team storage: Per person | 18 | 0.125 | 2.25
| General Practice (GP) Services | Staff zone | Staff WC: Ambulant | 2 | 2 | 4 | Staff may also use specimen WCs.
| General Practice (GP) Services | Staff zone | Staff WC: Accessible | 1 | 4.5 | 4.5 | Staff may also use specimen WCs.
| General Practice (GP) Services | Staff zone | Staff rest and mini kitchen: Per person | 30 | 1.8 | 54 | Assume 1 place per generic clinical room.
| General Practice (GP) Services | Staff zone | Staff changing/shower/lockers: Per person | 30 | 1.4 | 42 | Assume 1 place per generic clinical room.
| General Practice (GP) Services | Staff zone | Staff shower: Accessible | 1 | 6 | 6
| General Practice (GP) Services | Staff zone | Staff shower/change: Gender neutral: Accessible | 1 | 4.5 | 4.5
| General Practice (GP) Services | Staff zone | Staff lockers: Per person | 5 | 0.5 | 2.5
[5 empty] | Subtotal | 255.55
|  |  |  | Subtotal - GP Services |  | 1071.05
Community Care, Secondary Shift Clinics and Family Hub
Core | Community Care and Secondary Shift Clinics | Public | Waiting area allowance: Per person | 62 | 2 | 124 | Assumes 2 x people waiting per clinical room, and 8 x people waiting for group rooms.
| Community Care and Secondary Shift Clinics | Public | Waiting area allowance: Child/play area: Per person | 7 | 2 | 14 | Assumes 10% allowance for child/play area, or a minimum of 6m2, whichever is larger.
| Community Care and Secondary Shift Clinics | Public | Reception: Per person | 2 | 5.5 | 11 | Assumes 1 x reception space per 35 people.
| Community Care and Secondary Shift Clinics | Public | Self-check-in kiosk | 2 | 2.5 | 5 | Assumes 1 x self check-in per 35 people.
| Community Care and Secondary Shift Clinics | Public | WC: Semi-ambulant | 5 | 2.5 | 12.5
| Community Care and Secondary Shift Clinics | Public | WC: Accessible | 2 | 4.5 | 9
| Community Care and Secondary Shift Clinics | Public | Interview/quiet room (Small) | 2 | 8 | 16
[5 empty] | Subtotal | 191.5
Core+ | Family Hubs | Public - Discrete zone | Waiting area allowance: Child/play area: Per person | 22 | 2 | 44 | Assumes 2 x people waiting per clinical room, and 8 x people waiting for group rooms.
| Family Hubs | Public - Discrete zone | Waiting area allowance: Child/play area: Per person | 7 | 2 | 14 | Assume 30% allowance for child/play area.
| Family Hubs | Public - Discrete zone | Reception: Per person | 1 | 5.5 | 5.5 | Assumes 1 x reception space per 35 people.
| Family Hubs | Public - Discrete zone | Self-check-in kiosk | 1 | 2.5 | 2.5 | Assumes 1 x self check-in per 35 people.
| Family Hubs | Public - Discrete zone | WC: Semi-ambulant | 1 | 2.5 | 2.5
| Family Hubs | Public - Discrete zone | WC: Accessible | 2 | 4.5 | 9
[5 empty] | Subtotal | 77.5
Core+ | Family Hubs | Clinical zone | Consulting/examination room: Two-sided couch access | 2 | 13.5 | 27
| Family Hubs | Clinical zone | Consultation/treatment room: Three-sided couch access | 1 | 16 | 16
| Family Hubs | Clinical zone | Group room | 2 | 32.5 | 65
| Family Hubs | Clinical zone | Store: 5m2 | 1 | 5 | 5 | Group room storage (assume majority of equipment etc. stored in the room)
| Family Hubs | Clinical zone | Bay: Beverage | 1 | 3 | 3
| Family Hubs | Clinical zone | Specimen WC: Independent wheelchair | 1 | 4.5 | 4.5
| Family Hubs | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Clinical supplies
| Family Hubs | Clinical zone | Store: 8m2 | 1 | 8 | 8 | General store
[5 empty] | Subtotal | 136.5
Core | Community Care Cluster | Clinical zone | Consulting/examination room: Two-sided couch access | 2 | 13.5 | 27
| Community Care Cluster | Clinical zone | Consultation/treatment room: Three-sided couch access | 1 | 16 | 16
| Community Care Cluster | Clinical zone | Treatment room (Standard) | 4 | 16 | 64
| Community Care Cluster | Clinical zone | Treatment room (Bariatric) | 1 | 20 | 20
| Community Care Cluster | Clinical zone | Specimen WC: Independent wheelchair | 1 | 4.5 | 4.5
| Community Care Cluster | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Clinical Supplies.
| Community Care Cluster | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Equipment.
[5 empty] | Subtotal | 147.5
Core | Secondary Shift Clinics Cluster | Clinical zone | Treatment room (Standard) | 2 | 16 | 32 | 60% of required Treatment room provision.
| Secondary Shift Clinics Cluster | Clinical zone | Treatment room (Bariatric) | 1 | 20 | 20 | 40% of required Treatment room provision. Bariatric provision.
| Secondary Shift Clinics Cluster | Clinical zone | WC: Accessible | 1 | 4.5 | 4.5 | e.g. gynae patients
| Secondary Shift Clinics Cluster | Clinical zone | Patient change: Wheelchair accessible | 3 | 4.5 | 13.5 | 1 per Treatment room.
| Secondary Shift Clinics Cluster | Clinical zone | Recovery bay: Recliner/chair | 3 | 4.6 | 13.8 | 1 per Treatment room.
| Secondary Shift Clinics Cluster | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Clinical supplies.
| Secondary Shift Clinics Cluster | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Equipment.
[5 empty] | Subtotal | 99.8
Core++ | Diagnostics Cluster | Clinical zone | Treatment room (Standard) | 2 | 16 | 32 | Incl. US room.
| Diagnostics Cluster | Clinical zone | Treatment room (Bariatric) | 1 | 20 | 20
| Diagnostics Cluster | Clinical zone | Specimen WC: Independent wheelchair | 1 | 4.5 | 4.5
| Diagnostics Cluster | Clinical zone | Phlebotomy room | 3 | 8 | 24
| Diagnostics Cluster | Clinical zone | Patient change: Wheelchair accessible | 2 | 4.5 | 9
| Diagnostics Cluster | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Clinical supplies
| Diagnostics Cluster | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Equipment
[5 empty] | Subtotal | 105.5
Core++ | Community Care, Secondary Shift Clinics and Diagnostics | Shared Clinical zone | Pantry/refreshment area | 1 | 8 | 8
| Community Care, Secondary Shift Clinics and Diagnostics | Shared Clinical zone | Group room | 3 | 32.5 | 97.5 | Can be used flexibly as a seminar / MDT room.
| Community Care, Secondary Shift Clinics and Diagnostics | Shared Clinical zone | Store: 5m2 | 1.5 | 5 | 7.5 | Group room storage (assume majority of equipment etc. stored in the room)
[5 empty] | Subtotal | 113
Core++ | Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Clinical and non-clinical support zone | Clean utility (Small) | 4 | 8 | 32 | 1 per 12 C/E rooms or 1 per 4 treatment rooms
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Clinical and non-clinical support zone | Dirty utility (Small) | 4 | 8 | 32 | 1 per 12 C/E rooms or 1 per 4 treatment rooms
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Clinical and non-clinical support zone | Scrub bay | 3 | 4 | 12 | Shared, associated with treatment rooms. 1 per 4 treatment rooms
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Clinical and non-clinical support zone | Near patient testing room | 1 | 8 | 8
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Clinical and non-clinical support zone | Bay: Resus trolley | 2 | 2 | 4
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Clinical and non-clinical support zone | Store: Ready to use gas cylinders | 2 | 2 | 4
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Clinical and non-clinical support zone | Bay: Mobile imaging | 1 | 3 | 3
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Clinical and non-clinical support zone | Bay: Linen trolley | 1 | 3 | 3
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Clinical and non-clinical support zone | Disposal hold (Small) | 1 | 2 | 2
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Clinical and non-clinical support zone | Cleaner's room | 1 | 8 | 8
[5 empty] | Subtotal | 108
Core++ | Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Staff zone | Virtual consultation pod | 6 | 4.6 | 27.6 | Total requirement for services = 8. Assume 70% carried out in dedicated booths, 30% carried out within quiet rooms.
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Staff zone | Interview/quiet room (Small) | 2 | 8 | 16
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Staff zone | Office: 1 person | 1 | 8 | 8 | Community Care team lead.
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Staff zone | Office: 1 person | 1 | 8 | 8 | Secondary Shift Clinics team lead.
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Staff zone | Office: 1 person | 1 | 8 | 8 | Family Hub lead.
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Staff zone | Office: 1 person | 1 | 8 | 8 | Diagnostics lead.
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Staff zone | Hot desk area: Per desk | 21.6 | 5 | 108 | General administration. Assumes 0.8 x hot desk per generic clinical room to reflect 80% room utilisation. Combined allowance.
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Staff zone | Personal/team storage: Per person | 21.6 | 0.125 | 2.7
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Staff zone | Staff WC: Ambulant | 3 | 2 | 6 | Staff may also use specimen WCs.
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Staff zone | Staff WC: Accessible | 2 | 4.5 | 9 | Staff may also use specimen WCs.
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Staff zone | Staff rest and mini kitchen: Per person | 27 | 1.8 | 48.6 | Assume 1 place per generic clinical room. Combined allowance.
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Staff zone | Staff changing/shower/lockers: Per person | 27 | 1.4 | 37.8 | Assume 1 place per generic clinical room. Combined allowance.
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Staff zone | Staff shower: Accessible | 1 | 6 | 6
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Staff zone | Staff shower/change: Gender neutral: Accessible | 1 | 4.5 | 4.5
| Community Care, Secondary Shift Clinics, Family Hub & Diagnostics | Staff zone | Staff lockers: Per person | 8 | 0.5 | 4
[5 empty] | Subtotal | 302.2
|  |  | Subtotal - Community Care, Secondary Shift Clinics, Family Hubs & Diagnostics |  |  | 1281.5
Community Mental Health & Minor Injuries/Walk-ins
Core+ | Community Mental Health | Public - Discrete zone | Lobby: Main Entrance (Small) | 1 | 6 | 6
| Community Mental Health | Public - Discrete zone | Waiting area allowance: Per person | 14 | 2 | 28 | Assumes 2 x people waiting per clinical room, and 8 x people waiting for group rooms. Separation of adult / child mental health services required (if provided)
| Community Mental Health | Public - Discrete zone | Waiting area allowance: Child/play area: Per person | 3 | 2 | 6 | Assume 10% allowance for child/play area or minimum 6m2, whichever is larger. Separation of adult / child mental health services required (if provided)
| Community Mental Health | Public - Discrete zone | Reception: Per person | 1 | 5.5 | 5.5 | 1 per 35 people.
| Community Mental Health | Public - Discrete zone | WC: Semi-ambulant | 2 | 2.5 | 5 | Anti-ligature.
| Community Mental Health | Public - Discrete zone | WC: Accessible | 1 | 4.5 | 4.5 | Anti-ligature.
| Community Mental Health | Public - Discrete zone | Multisensory room | 1 | 10 | 10
[5 empty] | Subtotal | 65
Core+ | Minor Injuries / Walk-in | Public | Waiting area allowance: Per person | 14 | 2 | 28 | Assumes 2 per generic clinical space (incl. plaster room).
| Minor Injuries / Walk-in | Public | Waiting area allowance: Child/play area: Per person | 3 | 2 | 6 | Assume 10% allowance for child/play area or minimum 6m2, whichever is larger.
| Minor Injuries / Walk-in | Public | Reception: Per person | 1 | 5.5 | 5.5 | 1 per 35 people.
| Minor Injuries / Walk-in | Public | WC: Semi-ambulant | 1 | 2.5 | 2.5
| Minor Injuries / Walk-in | Public | WC: Accessible | 1 | 4.5 | 4.5
[5 empty] | Subtotal | 46.5
| Community Mental Health | Clinical zone | Interview/quiet room (Small) | 1 | 8 | 8
Core+ | Community Mental Health | Clinical zone | Consulting/examination room: Two-sided couch access | 1 | 13.5 | 13.5 | Assumes two-sided access is sufficient.
| Community Mental Health | Clinical zone | Group room | 1 | 32.5 | 32.5
| Community Mental Health | Clinical zone | Treatment room (Standard) | 1 | 16 | 16
| Community Mental Health | Clinical zone | Store: 5m2 | 1 | 5 | 5 | Group room storage.
| Community Mental Health | Clinical zone | Observation room | 1 | 8 | 8 | Adjacent to group room
| Community Mental Health | Clinical zone | Bay: Beverage | 1 | 3 | 3
| Community Mental Health | Clinical zone | WC: Accessible | 1 | 4.5 | 4.5 | Anti-ligature
| Community Mental Health | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Equipment/general store
| Community Mental Health | Clinical zone | Store: 8m2 | 1 | 8 | 8 | Clinical supplies
[5 empty] | Subtotal | 106.5
Core+ | Minor Injuries / Walk-in | Clinical zone | Consulting/examination room: Two-sided couch access | 1 | 13.5 | 13.5
| Minor Injuries / Walk-in | Clinical zone | Consultation/treatment room: Three-sided couch access | 1 | 16 | 16
| Minor Injuries / Walk-in | Clinical zone | Treatment room (Standard) | 4 | 16 | 64
| Minor Injuries / Walk-in | Clinical zone | Treatment room (Bariatric) | 1 | 20 | 20
| Minor Injuries / Walk-in | Clinical zone | Plaster room | 1 | 16 | 16
| Minor Injuries / Walk-in | Clinical zone | Store: Plaster room | 1 | 4 | 4
| Minor Injuries / Walk-in | Clinical zone | Specimen WC: Independent Wheelchair | 1 | 4.5 | 4.5
| Minor Injuries / Walk-in | Clinical and non-clinical support zone | Store: 8m2 | 1 | 8 | 8 | Clinical supplies
| Minor Injuries / Walk-in | Clinical and non-clinical support zone | Store: 8m2 | 1 | 8 | 8 | Equipment
[5 empty] | Subtotal | 154
Core+ | Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Bay: Resus trolley | 1 | 2 | 2
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Bay: Mobile imaging | 1 | 3 | 3 | Make accessible
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Clean utility (Small) | 2 | 8 | 16 | 1 per 12 C/E rooms or 1 per 4 treatment rooms
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Dirty utility (Small) | 2 | 8 | 16 | 1 per 12 C/E rooms or 1 per 4 treatment rooms
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Near patient testing room | 1 | 8 | 8
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Medicine store/preparation room | 1 | 12 | 12
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Bay: Linen trolley | 1 | 3 | 3
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Store: ready to use gas cylinders | 1 | 2 | 2
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Store: 10m2 | 1 | 10 | 10 | General/bulk store
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Disposal hold (Small) | 1 | 2 | 2
| Community Mental Health & Minor Injuries / Walk-in | Clinical and non-clinical support zone | Cleaner's room | 1 | 8 | 8
[5 empty] | Subtotal | 82
Core+ | Community Mental Health & Minor Injuries / Walk-in | Staff zone | Virtual consultation pod | 2 | 4.6 | 9.2 | Combined allowance.
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Office: 1 person | 1 | 8 | 8 | CMH Team lead
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Office: 1 person | 1 | 8 | 8 | Minor Injuries Team lead
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Hot desk area: Per desk | 9.6 | 5 | 48 | Assumes 0.8 x per generic clinical space incl. plaster room
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Personal/team storage: Per person | 9.6 | 0.125 | 1.2
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Staff WC: Ambulant | 2 | 2 | 4
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Staff WC: Accessible | 1 | 4.5 | 4.5
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Staff rest and mini kitchen: Per person | 12 | 1.8 | 21.6 | Assumes ~ 1 per generic clinical space.
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Staff changing/shower/lockers: Per person | 12 | 1.4 | 16.8 | Assumes 1 per generic clinical space.
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Staff shower: Accessible | 1 | 6 | 6
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Staff shower/change: Gender neutral: Accessible | 1 | 4.5 | 4.5
| Community Mental Health & Minor Injuries / Walk-in | Staff zone | Staff lockers: Per person | 5 | 0.5 | 2.5
[5 empty] | Subtotal | 134.3
|  |  | Subtotal - Community Mental Health & Minor Injuries / Walk-in |  |  | 588.3
FM Hub
Core+ | FM Hub | Non-clinical support zone | Disposal hold: 1700 litres | 1 | 8 | 8 | Shared across building.
| FM Hub | Non-clinical support zone | IT server/comms room (Large) | 1 | 40 | 40
[5 empty] | Subtotal | 48
[5 empty] | Total | 3135.85

## 2c) Integrated - Core ++
2c) Integrated - Core++ Services
Core functional content driven by the modelling
Typology | Service | Zone | Room name | Quantity | Size (m2) | Total size (m2) | Comments
Main Entrance
Core++ | Main Entrance | Public | Lobby: Main entrance (Large) | 1 | 10 | 10
| Main Entrance | Public | External canopy shelter: Mobility scooter/pram (Medium) | 0 | 12 | 0 | External.
| Main Entrance | Public | Changing places | 1 | 12 | 12
| Main Entrance | Public | Nappy change room | 1 | 5 | 5
| Main Entrance | Public | Infant feeding room | 1 | 5.5 | 5.5
| Main Entrance | Public | Multi-faith room | 1 | 8 | 8
| Main Entrance | Public | Waiting area allowance: Per person | 124 | 2 | 248 | Assumes 2 people per generic clinical space (incl. Phleb) and 8 per group room
| Main Entrance | Public | Waiting area allowance: Child/play area: Per person | 13 | 2 | 26 | Assume 10% provision for childrens/play area
| Main Entrance | Public | Reception: Per person | 4 | 5.5 | 22 | ~ 1 per 35 people
| Main Entrance | Public | Self-check-in kiosk | 4 | 2.5 | 10 | ~ 1 per 35 people
| Main Entrance | Public | WC: Semi-ambulant | 3 | 2.5 | 7.5
| Main Entrance | Public | WC: Accessible | 2 | 4.5 | 9
| Main Entrance | Public | Patient information/resource centre | 1 | 16 | 16
| Main Entrance | Public | Interview/quiet room (Small) | 3 | 8 | 24
| Main Entrance | Public | Store: 20m2 | 1 | 20 | 20 | Third sector storage
| Main Entrance | Public - Mental Health | Lobby: Main Entrance (Small) | 1 | 6 | 6
| Main Entrance | Public - Mental Health | Waiting area allowance: Per person | 7 | 2 | 14
| Main Entrance | Public - Mental Health | Waiting area allowance: Child/play area: Per person | 3 | 2 | 6
| Main Entrance | Public - Mental Health | Reception: Per person | 1 | 5.5 | 5.5
| Main Entrance | Public - Mental Health | WC: Accessible | 1 | 4.5 | 4.5 | Anti ligature
| Main Entrance | Public - Mental Health | Multisensory room | 1 | 10 | 10
| Main Entrance | Public | Community pharmacy (allowance) | 0 | 150 | 0
[5 empty] | Subtotal | 469
Core++ | Clinical | Clinical zone | Interview/quiet room (Small) | 2 | 8 | 16
| Clinical | Clinical zone | Consulting/examination room: Two-sided couch access | 13 | 13.5 | 175.5
| Clinical | Clinical zone | Consultation/treatment room: Three-sided couch access | 3 | 16 | 48
| Clinical | Clinical zone | Treatment room (Standard) | 12 | 16 | 192
| Clinical | Clinical zone | Treatment room (Bariatric) | 2 | 20 | 40
| Clinical | Clinical zone | Group room | 6 | 32.5 | 195 | Can be used flexibly as a seminar / MDT room
| Clinical | Clinical zone | Pantry/refreshment area | 1 | 8 | 8 | Where more than 2 group rooms are provided
| Clinical | Clinical zone | Store: 5m2 | 6 | 5 | 30 | Group room storage
| Clinical | Clinical zone | Bay: Beverage | 2 | 3 | 6
| Clinical | Clinical zone | Observation room | 1 | 8 | 8 | Mental health - adjoined to group room
| Clinical | Clinical zone | Specimen WC: Independent wheelchair | 3 | 4.5 | 13.5 | Assume 1 per floor
| Clinical | Clinical zone | Patient change: Wheelchair accessible | 2 | 4.5 | 9 | Assume ~30% of treatment room activity
| Clinical | Clinical zone | Patient change: Ambulant | 2 | 3 | 6
| Clinical | Clinical zone | Recovery bay: Recliner/chair | 4 | 4.6 | 18.4 | Assume ~30% of treatment room activity
| Clinical | Clinical zone | Phlebotomy room | 3 | 8 | 24
| Clinical | Clinical zone | WC: Accessible | 1 | 4.5 | 4.5 | Anti ligature
| Clinical | Clinical zone | Scrub bay | 4 | 4 | 16 | Associated with treatment rooms. ~ 1 per 4
[5 empty] | Subtotal | 809.9
Core++ | Clinical and non-clinical support | Clinical and non-clinical support zone | Clean utility (Small) | 4 | 8 | 32 | 1 per 4 treatment rooms
| Clinical and non-clinical support | Clinical and non-clinical support zone | Dirty utility (Small) | 4 | 8 | 32 | 1 per 4 treatment rooms
| Clinical and non-clinical support | Clinical and non-clinical support zone | Near patient testing room | 1 | 8 | 8
| Clinical and non-clinical support | Clinical and non-clinical support zone | Medicine store/preparation room | 1 | 12 | 12
| Clinical and non-clinical support | Clinical and non-clinical support zone | Bay: Resus trolley | 3 | 2 | 6
| Clinical and non-clinical support | Clinical and non-clinical support zone | Bay: Mobile imaging | 3 | 3 | 9
| Clinical and non-clinical support | Clinical and non-clinical support zone | Bay: Linen trolley | 3 | 3 | 9
| Clinical and non-clinical support | Clinical and non-clinical support zone | Specimen reception | 3 | 4 | 12
| Clinical and non-clinical support | Clinical and non-clinical support zone | Store: 15m2 | 2 | 15 | 30 | Clinical supplies
| Clinical and non-clinical support | Clinical and non-clinical support zone | Store: Ready to use gas cylinders | 3 | 2 | 6
| Clinical and non-clinical support | Clinical and non-clinical support zone | Store: 25m2 | 1 | 25 | 25 | General store
| Clinical and non-clinical support | Clinical and non-clinical support zone | Store: 15m2 | 2 | 15 | 30 | Equipment
| Clinical and non-clinical support | Clinical and non-clinical support zone | Disposal hold (Small) | 3 | 2 | 6 | 1 per floor
| Clinical and non-clinical support | Clinical and non-clinical support zone | Disposal hold: 1700 litres | 1 | 8 | 8
| Clinical and non-clinical support | Clinical and non-clinical support zone | Cleaner's room | 2 | 8 | 16 | 1 per floor
| Clinical and non-clinical support | Clinical and non-clinical support zone | Plaster room | 1 | 16 | 16
| Clinical and non-clinical support | Clinical and non-clinical support zone | Store: Plaster room | 1 | 4 | 4
| Clinical and non-clinical support | Clinical and non-clinical support zone | IT server/comms room (Large) | 1 | 40 | 40
[5 empty] | Subtotal | 301
Core++ | Hot zone | Hot zone | Staff shower/change: Gender neutral: Accessible | 1 | 4.5 | 4.5
| Hot zone | Hot zone | Sluice | 1 | 6 | 6
| Hot zone | Hot zone | Lobby: Entrance (small) | 1 | 4 | 4
| Hot zone | Hot zone | Waiting area allowance: Per person | 6 | 2 | 12
[5 empty] | Subtotal | 26.5
Core++ | Staff zone | Staff zone | Virtual consultation pod | 11 | 4.6 | 50.6 | Modelled output = 15; Assume 70% carried out within booths, 30% within quiet rooms
| Staff zone | Staff zone | Office: 2 people | 4 | 12 | 48 | Service managers / team leads
| Staff zone | Staff zone | Office: 1 Person | 3 | 8 | 24 | Service managers / team leads
| Staff zone | Staff zone | Shared workspace | 28 | 8.3 | 232.4 | General administration. Assumes ~ 0.6 per clinical space incl. phlebotomy; 20% carried out in clinical rooms
| Staff zone | Staff zone | Personal/team storage: Per person | - | 0.125 |  | 1 x provided per workspace (28) included in above overall shared workspace allowance
| Staff zone | Staff zone | Photocopy/storage | - | 6 |  | 1 x included in above overall shared workspace allowance
| Staff zone | Staff zone | Interview/quiet room (Small) | - | 8 |  | 4 x included in above overall shared workspace allowance
| Staff zone | Staff zone | Quiet room | - | 6 |  | 5 x included in above overall shared workspace allowance
| Staff zone | Staff zone | Collaborative spaces | - | 0.75 |  | 1 x provided per workspace (28) included in above overall shared workspace allowance
| Staff zone | Staff zone | Clinical touchdown: Per person | 9 | 3 | 27 | Assumes 0.2 additional allowance per clinical room, rounded to nearest whole number.
| Staff zone | Staff zone | Staff WC: Ambulant | 9 | 2 | 18 | 9nr Staff WCs total required under BS 6465 for 110nr staff (11nr if in self-contained washrooms)
| Staff zone | Staff zone | Staff WC: Accessible | 2 | 4.5 | 9
| Staff zone | Staff zone | Staff rest: Ambulant dining/seating | 39 | 1.5 | 58.5 | Assumes 110 staff, and provides accommodation for 40% occupation = 44 total (5 x wheelchair places)
| Staff zone | Staff zone | Staff rest: Wheelchair places | 5 | 3 | 15
| Staff zone | Staff zone | Staff kitchen | 1 | 12 | 12
| Staff zone | Staff zone | Staff lockers: Per person | 11 | 1.4 | 15.4 | Lockers BREEAM TRA 03 - 1nr locker per 10 staff
| Staff zone | Staff zone | Staff shower/change: Gender neutral: Accessible | 1 | 4.5 | 4.5
| Staff zone | Staff zone | Staff changing/shower/lockers: Per person | 44 | 1.4 | 61.6 | Assumes 1 per clinical space incl. phlebotomy.
[5 empty] | Subtotal | 576
[5 empty] | Total | 2182.4

## Standard rooms list (hidden)
Generic Standard room name | Size (m2) | Comments
Lobby: Main Entrance (Small) | 6
Lobby: Main Entrance (Medium) | 8
External canopy shelter: Mobility scooter/pram (Small) | 8
External canopy shelter: Mobility scooter/pram (Medium) | 12
Changing places | 12
Nappy change room | 5
Infant feeding room | 5.5 | Allows two people with a baby to use this space comfortably. A parent/carer with a double buggy (1040 mm long by 800 mm wide) can manoeuvre in and out of this room. May be used as a multi-faith room in smaller schemes.
Waiting area allowance: Per person | 2 | Enables these spaces to have a mixture of seating – including easy and bariatric chairs – and to accommodate the necessary circulation space to manoeuvre in the waiting area, with 10% of spaces to be suitable for people in wheelchairs.
Waiting area allowance: Child/play area: Per person | 2 | Minimum recommended size of 6m2.
Reception: Per person | 5.5 | Includes allowance for a local printer to be located here.
Self-check-in kiosk | 2.5
Patient information/resource centre | 16 | The space may contain a mixture of tables, chairs, computer workstations and bookshelves. Display or leaflet stands or shelves may be provided. The size of the area will depend on the number/type of users, range of display information, whether the area is staffed or not, and whether it is an enclosed space or open bay. A suggestion for sizing the space would be 16 m2. This space will be used by: • 1–2 patients • 1 staff member (if resourced) • 1–2 others
Consulting room (Small) | 8 | 2–3 occupants.
Consulting room (Medium) | 12 | 5–6 occupants. Can also support multidisciplinary team (MDT) activities.
Consultation/treatment room: Three-sided couch access | 16 | The consulting/examination room is intended as a flexible space for consultations and examinations, for use by a wide range of clinical specialties. The following procedures may take place in this room: • non-invasive procedures, i.e. procedures that do not break the skin (for example, changing a dressing) • minimally invasive procedures i.e. procedures that break or puncture the skin (for example, injections, taking blood)
Consulting/examination room: Two-sided couch access | 13.5
Interview/quiet room (Small) | 8 | The room may also be used as a quiet space where difficult conversations can take place in a calm environment or to provide respite from over stimulation if sensory-sensitive. The room should have appropriate sound insulation.
Interview/quiet room (Medium) | 12
Virtual consultation pod | 4.6 | E-consult pod with a glazed sliding door (generally for single occupancy but with provision for an additional supporting occupant)
Virtual consultation room | 8 | Up to 3 occupants
Treatment room (Standard) | 16 | Three-sided or all-round couch access
Treatment room (Large) | 18 | Three-sided couch access
Treatment room (Bariatric) | 20 | All-round couch access - bariatric activity
Recovery bay: Recliner/chair | 4.6 | For dressed patients
Recovery bay: Trolley | 9 | Gowned patients
Plaster room | 16
Store: Plaster room | 4
Group room | 32.5
Medicine store/preparation room | 12
Bay: Wheelchair parking | 4
WC: Accessible | 4.5
WC: Semi-ambulant | 2.5
Bay: Vending machines | 3
Clinical measurement room | 8
Near patient testing room | 8
Disposal hold: 1700 litres | 8
Cleaner's room | 8
Cleaner's cupboard | 5
Pantry/refreshment area | 8 | Provided if more than 2 group rooms
Specimen reception | 4
Specimen WC: Independent wheelchair | 4.5 | 1 per specimen reception.
Office: 1 person | 8
Office: 2 people | 12
Hot desk area: Per desk | 5
Staff WC: Ambulant | 2
Staff WC: Accessible | 4.5
Staff rest and mini kitchen: Per person | 1.8 | Size based on number of seats. Assume 1 place per generic clincial room.
Staff changing/shower/lockers: Per person | 1.4
Bay: Resus trolley | 2
Bay: Linen trolley | 3
Bay: Beverage | 3
General storage allowance | 2 | 2m2 per clinical room
Store: 5m2 | 5
Store: 8m2 | 8
Store: 10m2 | 10
Store: 15m2 | 15
Clean utility (Small) | 8
Clean utility (Medium) | 12
Dirty utility (Small) | 8
Dirty utility (Medium) | 12
Sluice | 6
Disposal hold (Small) | 2
Clinical touchdown: Per person | 3
Patient change: Wheelchair accessible | 4.5
Store: Ready to use gas cylinders | 2
Multisensory room | 10
Lobby: Entrance (Small) | 4
Observation room | 8
Bay: Mobile imaging | 3
Phlebotomy room | 8
Multi-faith room | 8
Lobby: Main entrance (Large) | 10
Scrub bay | 4
IT server/comms room (Small) | 20
IT server/comms room (Medium) | 30
IT server/comms room (Large) | 40
Staff shower: Accessible | 6
Staff shower/change: Gender neutral: Accessible | 4.5
Staff lockers: Per person | 0.5

## WC provision - WIP (hidden)
Number of people | Number of Ambulant WCs | Number of Accessible WCs | BS6465-1 Total WC's General | BS6465-1 Total WC's 50/50 M/F split (120%) | Column1 | BS6465-1 Total WC's Separate with basin 25% uplift | Column2
|  |  |  | Calculation | Actual | Calculation | Actual
1 | 0 | 1 | 1 | 1.2 | 2 | 1.25 | 2
2 | 0 | 1 | 1 | 1.2 | 2 | 1.25 | 2
3 | 0 | 1 | 1 | 1.2 | 2 | 1.25 | 2
4 | 0 | 1 | 1 | 1.2 | 2 | 1.25 | 2
5 | 0 | 1 | 1 | 1.2 | 2 | 1.25 | 2
6 | 1 | 1 | 2 | 2.4 | 3 | 2.5 | 3
7 | 1 | 1 | 2 | 2.4 | 3 | 2.5 | 3
8 | 1 | 1 | 2 | 2.4 | 3 | 2.5 | 3
9 | 1 | 1 | 2 | 2.4 | 3 | 2.5 | 3
10 | 1 | 1 | 2 | 2.4 | 3 | 2.5 | 3
11 | 1 | 1 | 2 | 2.4 | 3 | 2.5 | 3
12 | 1 | 1 | 2 | 2.4 | 3 | 2.5 | 3
13 | 1 | 1 | 2 | 2.4 | 3 | 2.5 | 3
14 | 1 | 1 | 2 | 2.4 | 3 | 2.5 | 3
15 | 1 | 1 | 2 | 2.4 | 3 | 2.5 | 3
16 | 2 | 1 | 3 | 3.6 | 4 | 3.75 | 4
17 | 2 | 1 | 3 | 3.6 | 4 | 3.75 | 4
18 | 2 | 1 | 3 | 3.6 | 4 | 3.75 | 4
19 | 2 | 1 | 3 | 3.6 | 4 | 3.75 | 4
20 | 2 | 1 | 3 | 3.6 | 4 | 3.75 | 4
21 | 2 | 1 | 3 | 3.6 | 4 | 3.75 | 4
22 | 2 | 1 | 3 | 3.6 | 4 | 3.75 | 4
23 | 2 | 1 | 3 | 3.6 | 4 | 3.75 | 4
24 | 2 | 1 | 3 | 3.6 | 4 | 3.75 | 4
25 | 2 | 1 | 3 | 3.6 | 4 | 3.75 | 4
26 | 2 | 1 | 3 | 3.6 | 4 | 3.75 | 4
27 | 2 | 1 | 3 | 3.6 | 4 | 3.75 | 4
28 | 2 | 1 | 3 | 3.6 | 4 | 3.75 | 4
29 | 2 | 1 | 3 | 3.6 | 4 | 3.75 | 4
30 | 2 | 1 | 3 | 3.6 | 4 | 3.75 | 4
31 | 3 | 1 | 4 | 4.8 | 5 | 5 | 5
32 | 3 | 1 | 4 | 4.8 | 5 | 5 | 5
33 | 3 | 1 | 4 | 4.8 | 5 | 5 | 5
34 | 3 | 1 | 4 | 4.8 | 5 | 5 | 5
35 | 3 | 1 | 4 | 4.8 | 5 | 5 | 5
36 | 3 | 1 | 4 | 4.8 | 5 | 5 | 5
37 | 3 | 1 | 4 | 4.8 | 5 | 5 | 5
38 | 3 | 1 | 4 | 4.8 | 5 | 5 | 5
39 | 3 | 1 | 4 | 4.8 | 5 | 5 | 5
40 | 3 | 1 | 4 | 4.8 | 5 | 5 | 5
41 | 3 | 1 | 4 | 4.8 | 5 | 5 | 5
42 | 3 | 1 | 4 | 4.8 | 5 | 5 | 5
43 | 3 | 1 | 4 | 4.8 | 5 | 5 | 5
44 | 3 | 1 | 4 | 4.8 | 5 | 5 | 5
45 | 3 | 1 | 4 | 4.8 | 5 | 5 | 5
46 | 3 | 2 | 5 | 6 | 6 | 6.25 | 7
47 | 3 | 2 | 5 | 6 | 6 | 6.25 | 7
48 | 3 | 2 | 5 | 6 | 6 | 6.25 | 7
49 | 3 | 2 | 5 | 6 | 6 | 6.25 | 7
50 | 3 | 2 | 5 | 6 | 6 | 6.25 | 7
51 | 3 | 2 | 5 | 6 | 6 | 6.25 | 7
52 | 3 | 2 | 5 | 6 | 6 | 6.25 | 7
53 | 3 | 2 | 5 | 6 | 6 | 6.25 | 7
54 | 3 | 2 | 5 | 6 | 6 | 6.25 | 7
55 | 3 | 2 | 5 | 6 | 6 | 6.25 | 7
56 | 3 | 2 | 5 | 6 | 6 | 6.25 | 7
57 | 3 | 2 | 5 | 6 | 6 | 6.25 | 7
58 | 3 | 2 | 5 | 6 | 6 | 6.25 | 7
59 | 3 | 2 | 5 | 6 | 6 | 6.25 | 7
60 | 3 | 2 | 5 | 6 | 6 | 6.25 | 7
61 | 4 | 2 | 6 | 7.2 | 8 | 7.5 | 8
62 | 4 | 2 | 6 | 7.2 | 8 | 7.5 | 8
63 | 4 | 2 | 6 | 7.2 | 8 | 7.5 | 8
64 | 4 | 2 | 6 | 7.2 | 8 | 7.5 | 8
65 | 4 | 2 | 6 | 7.2 | 8 | 7.5 | 8
66 | 4 | 2 | 6 | 7.2 | 8 | 7.5 | 8
67 | 4 | 2 | 6 | 7.2 | 8 | 7.5 | 8
68 | 4 | 2 | 6 | 7.2 | 8 | 7.5 | 8
69 | 4 | 2 | 6 | 7.2 | 8 | 7.5 | 8
70 | 4 | 2 | 6 | 7.2 | 8 | 7.5 | 8
71 | 4 | 2 | 6 | 7.2 | 8 | 7.5 | 8
72 | 4 | 2 | 6 | 7.2 | 8 | 7.5 | 8
73 | 4 | 2 | 6 | 7.2 | 8 | 7.5 | 8
74 | 4 | 2 | 6 | 7.2 | 8 | 7.5 | 8
75 | 4 | 2 | 6 | 7.2 | 8 | 7.5 | 8
76 | 5 | 2 | 7 | 8.4 | 9 | 8.75 | 9
77 | 5 | 2 | 7 | 8.4 | 9 | 8.75 | 9
78 | 5 | 2 | 7 | 8.4 | 9 | 8.75 | 9
79 | 5 | 2 | 7 | 8.4 | 9 | 8.75 | 9
80 | 5 | 2 | 7 | 8.4 | 9 | 8.75 | 9
81 | 5 | 2 | 7 | 8.4 | 9 | 8.75 | 9
82 | 5 | 2 | 7 | 8.4 | 9 | 8.75 | 9
83 | 5 | 2 | 7 | 8.4 | 9 | 8.75 | 9
84 | 5 | 2 | 7 | 8.4 | 9 | 8.75 | 9
85 | 5 | 2 | 7 | 8.4 | 9 | 8.75 | 9
86 | 5 | 2 | 7 | 8.4 | 9 | 8.75 | 9
87 | 5 | 2 | 7 | 8.4 | 9 | 8.75 | 9
88 | 5 | 2 | 7 | 8.4 | 9 | 8.75 | 9
89 | 5 | 2 | 7 | 8.4 | 9 | 8.75 | 9
90 | 5 | 2 | 7 | 8.4 | 9 | 8.75 | 9
91 | 5 | 3 | 8 | 9.6 | 10 | 10 | 10
92 | 5 | 3 | 8 | 9.6 | 10 | 10 | 10
93 | 5 | 3 | 8 | 9.6 | 10 | 10 | 10
94 | 5 | 3 | 8 | 9.6 | 10 | 10 | 10
95 | 5 | 3 | 8 | 9.6 | 10 | 10 | 10
96 | 5 | 3 | 8 | 9.6 | 10 | 10 | 10
97 | 5 | 3 | 8 | 9.6 | 10 | 10 | 10
98 | 5 | 3 | 8 | 9.6 | 10 | 10 | 10
99 | 5 | 3 | 8 | 9.6 | 10 | 10 | 10
100 | 5 | 3 | 8 | 9.6 | 10 | 10 | 10
Above 100 |  |  | 8 plus 1 for every unit or fraction of 25 persons

## BREEAM TRA03 - WIP (hidden)
| Staff numbers | Cycle Space | Lockers | Showers
1 cycle space per 10 staff | 1-10 staff | 1 | 1 | 1
1 shower per 10 cycle space (100 staff) | 11-20 | 2 | 2 | 1
1 locker per cycle space | 21-30 | 3 | 3 | 1
| 31-40 | 4 | 4 | 1
No of cycle spaces for healthcare | 41-50 | 5 | 5 | 1
| 51-60 | 6 | 6 | 1
| 61-70 | 7 | 7 | 1
| 71-80 | 8 | 8 | 1
| 81-90 | 9 | 9 | 1
| 91-100 | 10 | 10 | 1
| 101-110 | 11 | 11 | 2
| 111-120 | 12 | 12 | 2
| 121-130 | 13 | 13 | 2
| 131-140 | 14 | 14 | 2
| 141-150 | 15 | 15 | 2
| 151-160 | 16 | 16 | 2
| 161-170 | 17 | 17 | 2
| 171-180 | 18 | 18 | 2
| 181-190 | 19 | 19 | 2
| 191-200 | 20 | 20 | 2
| 201 210 | 21 | 21 | 3
| 211-220 | 22 | 22 | 3
| 221-230 | 23 | 23 | 3
| 231-240 | 24 | 24 | 3
| 241-250 | 25 | 25 | 3
| 251-260 | 26 | 26 | 3
| 261-270 | 27 | 27 | 3
| 271-280 | 28 | 28 | 3
| 281-290 | 29 | 29 | 3
| 291-300 | 30 | 30 | 3