## B0
B0 record of tests undertaken |  |  | Signed of by
|  | Completed | MCR | CP | AP | QC | AE | Comments
B1 | Design sign-off by the MGSG | Yes/No | N/A | N/A
B2 | Brazing inspections | Yes/No |  |  |  | N/A | N/A
B3 | Snagging and record of interim inspections | Yes/No |  |  |  | N/A
B4 | Labelling and marking, sleeving and supports | Yes/No |  |  |  | N/A | N/A
B5 | Carcass pressure test | Yes/No |  |  |  | N/A | N/A
B6 | Verification of drawings | Yes/No |  |  |  | N/A
B7 | HTM compliance | Yes/No |  |  |  | N/A
B8a | Plantroom compliance | Yes/No |  |  |  | N/A | N/A
B8b | Manifold room compliance | Yes/No |  |  |  | N/A | N/A
B8c | Cylinder store compliance | Yes/No |  |  |  | N/A | N/A
B9 | Air plant | Yes/No | N/A |  |  | N/A | N/A
B10 | Pressure-reducing stations (PRS) | Yes/No | N/A |  |  | N/A | N/A
B11 | Vacuum Plant | Yes/No | N/A |  |  | N/A | N/A
B12 | AGSS Plant | Yes/No | N/A |  |  | N/A | N/A
B13 | Manifold systems | Yes/No | N/A |  |  | N/A | N/A
B14 | Liquid systems | Yes/No | N/A |  |  | N/A | N/A
B15 | PSSR 2000 documentation | Yes/No | N/A |  |  | N/A
B16 | Second-fix items installed | Yes/No | N/A |  |  | N/A | N/A
B17 | "Do not use" plugs installed | Yes/No | N/A |  |  | N/A | N/A
B18 | Pipeline pressure test | Yes/No | N/A |  |  | N/A | N/A
B19 | Vacuum leak test | Yes/No | N/A |  |  | N/A | N/A
B20 | Engineer's particulate test | Yes/No | N/A |  |  | N/A | N/A
B21 | Cross-connection test | Yes/No | N/A |  |  | N/A | N/A
B22 | LVAs (zoning, closure, identity and gas specifity) | Yes/No | N/A |  |  | N/A | N/A
B23 | AVSUs (zoning, closure, identity and gas specifity, signage) | Yes/No | N/A |  |  | N/A | N/A
B24 | Terminal unit tests | Yes/No | N/A |  |  | N/A | N/A
B25 | Purging and filling | Yes/No | N/A |  |  |  | N/A
B26 | Design flow performance tests | Yes/No | N/A |  |  | N/A | N/A
B27 | Plant alarm tests | Yes/No | N/A |  |  | N/A | N/A
B28 | Local alarm tests | Yes/No | N/A |  |  | N/A | N/A
B29 | QC particulate tests | Yes/No | N/A | N/A |  |  | N/A
B30 | QC identity and quality tests | Yes/No | N/A | N/A |  |  | N/A
B31 | Key register | Yes/No | N/A |  |  | N/A | N/A
B32 | "Do not use" plugs removed | Yes/No | N/A |  |  | N/A | N/A
B33 | Completion certificate | Yes/No
|  |  | Sign |  |  | Print |  | Date
Competent Person MGPS
Mechanical Contractor
Quality Controller (MGPS)
Authorising Engineer (MGPS)

## B1
B1 | Design sign-off by the MGSG
The piped medical gas design has been checked for compliance with the relevant parts of HTM 02-01 and the following specifications and drawings.
|  |  | Date | Specification reference
Specification reference/s
Register of design drawings
|  | Reference | Description | Reason
1
2
3
4
5
6
7
8
9
10
The following derogations have been agreed and accepted:
Register of derogations from HTM 02-01
|  | Reference | Description | Reason
1
2
3
4
5
All of the above has been agreed by the Medical Gas Safety Group.
|  |  | Signed | Print | Date
Chair of the MGSG
Authorising Engineer (MGPS)
Authorised Person (MGPS)
Quality Controller (MGPS)

## B2
B2 Brazing inspections
No. | Date | Location | Gas | Pipeline size | Type of fitting | Penetration | Cleanliness | Initial
[6 empty] | Pass/Fail | Pass/Fail | AP (MGPS) | CP (MGPS)
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
| All joint inspections completed |  | Yes/No | [5 empty] | Sheet 1 of
|  |  |  | Signed |  | Print |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)
Mechanical Contractor

## B3
B3 Snagging and record of interim inspections
Initial
Date | Area inspected | Drawing reference | Issue |  | Rectified | Date | MCR | AP (MGPS) | CP (MGPS)
| All joint inspections completed |  | Yes/No |  |  |  |  | Sheet 1 of
|  | Signed |  | Print |  |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)
Mechanical Contractor

## B4
B4 Labelling and marking, sleeving and supports
No. | Date | Gases | Gas identification | Flow arrows | Dual circuit identification | Sleeving | Supports | Location inspected
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
| All inspections completed |  |  | Yes/No |  |  |  | Sheet 1 of
|  |  |  | Signed |  | Print |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)
Mechanical Contractor
5

## B5
B5 Carcass pressure test
Description of the extent of the pipeline to be tested:
Gas pipeline to be tested |  |  | Gas used to test
Test pressure to be applied
Duration of the test
Test gauge identification
Test gauge certificate number
Actual test pressure on commencement |  |  | Test start time
Actual test pressure on completion |  |  | Test stop time
| All tests completed | Yes/No |  | Sheet 1 of
|  | Signed | Print | Date
Authorised Person (MGPS)
Competent Person (MGPS)
Mechanical Contractor

## B6
B6 Verification of drawings
No. | Date | Drawing reference | Description | Initial
|  |  |  | AP (MGPS) | CP (MGPS)
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
All drawings completed |  |  | Yes/No |  | Sheet 1 of
|  |  | Signed | Print |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)
Mechanical Contractor
Authorising Engineer (MGPS)

## B7
B7 HTM compliance
The following installation has been inspected in line with forms B1 and B6:
Drawing number | Gases | [11 empty] | Installation compliant
| O2 | N2O | O2/N2O | MA4 | SA7 | VAC | CO2 | AGS | DA | DVAV | DAGS | Other | MCR | CP (MGPS) | AP (MGPS) | IEA(AE)
| All areas completed |  |  | Yes/No | [10 empty] | Sheet 1 of
[5 empty] | Signed |  |  |  | Print |  |  |  | Date
Mechanical Contractor
Competent Person (MGPS)
Authorised Person (MGPS)
Authorising Engineer (MGPS)

## B8a
B8a Plantroom compliance
Gas
Description of plant
| Pass/Fail | Comments
Access to plantroom
External signage
External lighting
External security
Internal signage
Internal lighting
Heating
Ventilation
Cleanliness
Segregation of plant
Plant space for access
All inspections completed |  | Yes/No |  | Sheet 1 of
|  | Sign | Print | Date
Authorised Person (MGPS)
Competent Person (MGPS)
Mechanical Contractor

## B8b
B8b Manifold room compliance
Gas
Description of manifold/s
| Pass/Fail | Comments
Access to manifold room
External signage
External lighting
External security
Internal signage
Internal lighting
Heating
Ventilation
Cleanliness
All cylinders secure
Spare cylinder racking
All inspections completed |  | Yes/No |  | Sheet 1 of
|  | Signed | Print |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)
Mechanical Contractor

## B8c
B8c Cylinder store compliance
| Cylinder store type |  | Main | External/Internal |  | Satellite
|  | Pass/Fail | Comments
Access to cylinder store
External signage
External lighting
External security
Internal signage
Internal lighting
Heating
Ventilation
Cleanliness
All cylinders secure
Spare cylinder racking
Gas |  | Cylinder size | Quantity | Full | Empty | Comments
All inspections completed |  |  | Yes/No |  |  |  | Sheet 1 of
|  |  | Sign |  |  | Print | Date
Authorised Person (MGPS)
Competent Person (MGPS)
Mechanical Contractor

## B9
B9 Air plant
Type of plant | Medical* | Surgical* | Combined* | Dental*
Compressors | Compressor 1 | Compressor 2 | Compressor 3 | Compressor 4 | Compressor 5 | Compressor 6
Type
Size
Identification
|  |  |  | Tested | Yes/No | Pass/Fail
Notes
Vessels | Vessel 1 | Vessel 2 | Vessel 3 | Vessel 4
Type
Size
Identification
Tested | Yes/No | Pass/Fail
Oil–water separator installed and connected to drains |  |  | Yes/No
Notes
Dryers | Dryer 1 RHS | Dryer 1 LHS | Dryer 2 RHS | Dryer 2 LHS
Type
Size
Identification
|  |  | Tested | Yes/No | Pass/Fail
Notes
Individual tests to be recorded on the CP documentation and supplied with this B form.
All tests completed |  |  | Yes/No
|  | Signed |  | Print |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)
Mechanical Contractor

## B10
B10 Pressure-reducing stations (PRS)
Air supply from plant:
Supply to departments:
Regulator 1 | Duty* | Standby*
Input pressure | kPa |  | Output pressure |  |  | kPa
Regulator 2 | Duty* | Standby*
Input pressure | kPa |  | Output pressure |  |  | kPa
All valves in the open position |  |  |  | Pass | Fail
Pressure safety valves piped to a safe location |  |  |  | Pass | Fail
Exhaust warning signage installed for pressure gas |  |  |  | Pass | Fail
Pressure guages clear and visible |  |  |  | Pass | Fail
Test points accessible and compliant |  |  |  | Pass | Fail
Alarm tested for high and low pressure |  |  |  | Pass | Fail
System identification clear and correct |  |  |  | Pass | Fail
Individual tests to be recorded on the CP documentation and supplied with this B form.
All tests completed |  | Yes/No |  | Sheet 1 of
| Signed |  | Print |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)
Mechanical Contractor

## B11
B11 Vacuum plant
Type of plant | Medical* | Dental*
Pumps | Pump 1 | Pump 2 | Pump 3 | Pump 4 | Pump 5 | Pump 6
Type
Size
Identification
Tested | Yes/No | Pass/Fail
Notes
Vessels | Vessel 1 | Vessel 2 | Vessel 3 | Vessel 4
Type
Size
Identification
Tested | Yes/No | Pass/Fail
Notes
Bio filters | RHS |  | LHS
Type
Size
Identification
Tested | Yes/No |  | Pass/Fail
Notes
Individual tests to be recorded on the CP documentation and supplied with this B form.
All tests completed |  |  | Yes/No |  | Sheet 1 of
|  | Signed |  | Print |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)
Mechanical Contractor

## B12
B12 AGSS plant
Locations supplied
Type of plant | Medical* | Dental*
Pumps/Blower | Pump/Blower 1 |  | Pump/Blower 2
Type
Size
Identification
Balance valve
Balance valve filter
Tested | Yes/No |  | Pass/Fail
Notes
|  | Individual flow rate in L/min |  | System flow rate all terminal units in operation
Terminal unit | Static line pressure | 130 */80 * | 80*/ 50* | 130 */80 * | 80*/ 50*
1
2
3
4
5
6
Notes
Individual tests to be recorded on the CP documentation and supplied with this B form.
All tests completed |  |  | Yes/No |  | Sheet 1 of
|  | Signed |  | Print |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)
Mechanical Contractor

## B13
B13 Manifold systems
Manual change manifold
Primary* | Secondary* | Tertiary*
Gas
Number of cylinders
Locations supplied
Tested in accordance with manufacturers' requirements |  |  |  | Pass | Fail
Tested in accordance with HTM 02-01 |  |  |  | Pass | Fail
Spare cylinder racking for 1 bank = 1 cylinder installed |  |  |  | Pass | Fail
Notes
Automatic changeover manifold
Primary* | Secondary* | Tertiary*
Gas
Number of cylinders
Locations supplied
Tested in accordance with manufacturers' requirements |  |  |  | Pass | Fail
Tested in accordance with HTM 02-01 |  |  |  | Pass | Fail
Spare cylinder racking for 1 bank = 1 cylinder installed |  |  |  | Pass | Fail
Notes
Individual tests to be recorded on the CP documentation and supplied with this B form.
All tests completed |  |  | Yes/No |  | Sheet 1 of
|  | Signed |  | Print |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)

## B14
B14 Liquid systems
Description of system
Primary* | Secondary* | Tertiary*
Gas
Locations supplied
Tested in accordance with manufacturers' requirements |  |  |  | Pass | Fail
Tested in accordance with HTM 02-01 |  |  |  | Pass | Fail
Compound secure, lighting installed and clean |  |  |  | Pass | Fail
Signage and instructions posted internally and externally |  |  |  | Yes | No
Road markings and parking restrictions clear and present
Training received on the installation |  |  |  | Yes | No
Notes
Individual tests to be recorded on the CP documentation and supplied with this B form.
All tests completed |  |  | Yes/No |  | Sheet 1 of
|  | Signed |  | Print |  | Date
Authorised Person (MGPS)
Competent Person (MGPS) (system supplier)

## B15
B15 PSSR 2000 documentation
Item | Description |  |  | Unique ID | Pressure rating | Certificate supplied |  | Register completed |  | WSE completed
[6 empty] | Yes | No | Yes | No | Yes | No
[6 empty] | Yes | No | Yes | No | Yes | No
[6 empty] | Yes | No | Yes | No | Yes | No
[6 empty] | Yes | No | Yes | No | Yes | No
[6 empty] | Yes | No | Yes | No | Yes | No
[6 empty] | Yes | No | Yes | No | Yes | No
[6 empty] | Yes | No | Yes | No | Yes | No
[6 empty] | Yes | No | Yes | No | Yes | No
[6 empty] | Yes | No | Yes | No | Yes | No
[6 empty] | Yes | No | Yes | No | Yes | No
[6 empty] | Yes | No | Yes | No | Yes | No
[6 empty] | Yes | No | Yes | No | Yes | No
[6 empty] | Yes | No | Yes | No | Yes | No
[6 empty] | Yes | No | Yes | No | Yes | No
[6 empty] | Yes | No | Yes | No | Yes | No
[6 empty] | Yes | No | Yes | No | Yes | No
[6 empty] | Yes | No | Yes | No | Yes | No
[6 empty] | Yes | No | Yes | No | Yes | No
[6 empty] | Yes | No | Yes | No | Yes | No
All works completed |  | Yes/No | [7 empty] | Sheet 1 of
|  |  | Signed |  | Print |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)

## B16
B16 Second-fix items installed
The following second-fix components have been installed following the carcass tests, and the system is ready for pipeline commissioning.
Component |  | Location |  |  | Gas | Qty
Individual tests to be recorded on the CP documentation and supplied with this B form.
| All tests completed |  | Yes | No | Sheet 1 of
|  | Signed |  | Print | Date
Authorised Person (MGPS)
Competent Person (MGPS)

## B17
B17 "Do not use" plugs installed
Location |  | Gas | Number of terminal units | Plugs installed | AP (MGPS) initial
Page 1 of
| Signed |  | Print |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)

## B18
B18 Pipeline pressure test
| Gas | From |  |  | To
Pipeline to be tested:
Start pressure (kPa) |  |  | Final pressure (kPa)
Type of gauge |  |  | Time on test
Gauge number |  |  | Pressure differential
Gauge certificate | [5 empty] | Pass | Fail
| Gas | From |  |  | To
Pipeline to be tested:
Start pressure (kPa) |  |  | Final pressure (kPa)
Type of gauge |  |  | Time on test
Gauge number |  |  | Pressure differential
Gauge certificate | [5 empty] | Pass | Fail
| Gas | From |  |  | To
Pipeline to be tested:
Start pressure (kPa) |  |  | Final pressure (kPa)
Type of gauge |  |  | Time on test
Gauge number |  |  | Pressure differential
Gauge certificate | [5 empty] | Pass | Fail
Page 1 of
|  | Signed |  | Print |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)

## B19
B19 Vacuum leakage test
| Gas | From |  |  | To
Pipeline to be tested:
Start pressure (mmHG) |  |  | Final pressure (mmHG)
Type of gauge |  |  | Time on test
Gauge number |  |  | Pressure differential
Gauge certificate | [5 empty] | Pass | Fail
| Gas | From |  |  | To
Pipeline to be tested:
Start pressure (mmHG) |  |  | Final pressure (mmHG)
Type of gauge |  |  | Time on test
Gauge number |  |  | Pressure differential
Gauge certificate | [5 empty] | Pass | Fail
| Gas | From |  |  | To
Pipeline to be tested:
Start pressure (mmHG) |  |  | Final pressure (mmHG)
Type of gauge |  |  | Time on test
Gauge number |  |  | Pressure differential
Gauge certificate | [5 empty] | Pass | Fail
Page 1 of
|  | Signed |  | Print |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)

## B20
B20 Engineer's particulate test
Pipeline tested
Gas | From | To | Number of terminal units | Time of purge | Result
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
All tests completed |  | Yes/No |  | Sheet 1 of
|  | Signed | Print |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)

## B21
B21 Cross-connection test
Gas
Location of test
Pipeline from
Pipeline to
Cross-connections found |  | Yes | No | Pass | Fail
Gas
Location of test
Pipeline from
Pipeline to
Cross-connections found |  | Yes | No | Pass | Fail
Gas
Location of test
Pipeline from
Pipeline to
Cross-connections found |  | Yes | No | Pass | Fail
All tests completed | Yes/No |  |  |  | Sheet 1 of
| Signed |  | Print |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)
B21

## B22
B22 LVAs (zoning, closure, identity and gas specificity)
Valve number | Gas | Location | Closure | Zoning | NISTs | Signage | NISTs | Key | Valve | Key
|  |  | Pass/fail | Pass/fail | Pass/fail | Pass/fail | Locked | number | locked | number
|  | All tests completed |  |  | Yes/No |  | Sheet 1 of
|  |  |  | Signed |  | Print |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)
Mechanical Contractor

## B23
B23 AVSUs (zoning, closure, identity and gas specificity, signage)
Valve number | Gas | Location | Closure | Zoning | NISTs | Signage | Key
|  |  | Pass/fail | Pass/fail | Pass/fail | Pass/fail | Number
Schematic drawing of area controlled located at AVSU |  |  | Yes/No |  | Pass | Fail
Overall functionality of the AVSU |  |  | Yes/No |  | Pass | Fail
All tests completed |  |  | Yes / No |  | Sheet 1 of
|  | Signed | Print |  |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)
Mechanical Contractor

## B24
B24 Terminal unit tests
Location
Gas
Number of terminal units
Mechanical function tests |  | Pass | Fail
Flow and pressure tests |  | Pass | Fail
Individual tests to be recorded on the CP documentation and supplied with this B form.
Location
Gas
Number of terminal units
Mechanical function tests |  | Pass | Fail
Flow and pressure tests |  | Pass | Fail
Individual tests to be recorded on the CP documentation and supplied with this B form.
Location
Gas
Number of terminal units
Mechanical function tests |  | Pass | Fail
Flow and pressure tests |  | Pass | Fail
Individual tests to be recorded on the CP documentation and supplied with this B form.
All tests completed |  | Yes / No |  |  | Sheet 1 of
| Signed |  |  | Print | Date
Authorised Person (MGPS)
Competent Person (MGPS)

## B25
B25 Purging and filling test
Gas | Pipeline from |  | Pipeline to | Pipeline filled and purged with working gas
|  | Signed | Print | Date
Authorised Person (MGPS)
Competent Person (MGPS)
Quality Controller (MGPS)

## B26
B26 | Design flow performance tests
Gas
Description of the system
Design flowrate of the system |  |  |  |  | L/min
System static pressure
Location of bleed |  |  | Flowrate of bleed |  | Accumulative total
System pressure under full flow
Pressure loss under full flow
System design pressure loss
|  |  |  | Pass | Fail
All tests completed |  |  | Yes/No |  |  | Sheet 1 of
|  | Signed |  |  | Print | Date
Authorised Person (MGPS)
Competent Person (MGPS)

## B27
B27 | Plant alarm tests
Number of plant alarms
Locations
|  | Alarm 1 |  | Alarm 2 |  | Alarm 3 |  | Alarm 4
Battery backup tested |  | Pass | Fail | Pass | Fail | Pass | Fail | Pass | Fail
Battery date identified |  | Pass | Fail | Pass | Fail | Pass | Fail | Pass | Fail
Labelling completed |  | Pass | Fail | Pass | Fail | Pass | Fail | Pass | Fail
Audible signal tested |  | Pass | Fail | Pass | Fail | Pass | Fail | Pass | Fail
Automatic reset |  | Pass | Fail | Pass | Fail | Pass | Fail | Pass | Fail
All gases show correct alarms |  | Pass | Fail | Pass | Fail | Pass | Fail | Pass | Fail
All commissioning completed |  | Pass | Fail | Pass | Fail | Pass | Fail | Pass | Fail | 6
Individual tests to be recorded on the CP documentation and supplied with this B form.
All tests completed |  | Yes/No | [5 empty] | Sheet 1 of
|  | Signed |  |  | Print |  |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)

## B28
B28 | Local alarm tests
Alarm 1
Location of alarm
Location of transducers
Master alarm |  |  |  | Repeater alarm
Battery backup tested |  | Pass | Fail |  | Pass | Fail
Battery date identified |  | Pass | Fail |  | Pass | Fail
Labelling completed |  | Pass | Fail |  | Pass | Fail
Audible signal tested |  | Pass | Fail |  | Pass | Fail
Automatic reset |  | Pass | Fail |  | Pass | Fail
All gases show correct alarms |  | Pass | Fail |  | Pass | Fail
All commissioning completed |  | Pass | Fail |  | Pass | Fail
Alarm 2
Location of alarm
Location of transducers
Master alarm |  |  |  | Repeater alarm
Battery backup tested |  | Pass | Fail |  | Pass | Fail
Battery date identified |  | Pass | Fail |  | Pass | Fail
Labelling completed |  | Pass | Fail |  | Pass | Fail
Audible signal tested |  | Pass | Fail |  | Pass | Fail
Automatic reset |  | Pass | Fail |  | Pass | Fail
All gases show correct alarms |  | Pass | Fail |  | Pass | Fail
All commissioning completed |  | Pass | Fail |  | Pass | Fail
All tests completed |  | Yes / No |  |  | Sheet 1 of
|  | Signed |  | Print | Date
Authorised Person (MGPS)
Competent Person (MGPS)

## B29
B29 QC particulate test
Pipeline tested
Gas | AVSU number | Tested NIST or terminal unit | Number of terminal units/NISTs | Time of purge | Result
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
Pass/Fail
All tests completed |  | Yes No |  | Sheet 1 of
|  | Signed | Print |  | Date
Authorised Person (MGPS)
Quality Controller (MGPS)

## B30
B30 | QC identity and quality tests
QC test sheet supplied via the QC should be used as B30

## B31
B31 | Key register
Confirmation of the supply of correctly identified keys located in the master and Authorised Person's (MGPS) key cabinets
inline with the existing*/ new* key registration system has been completed.
An electronic copy of the updated key register has been supplied to the Authorised Person (MGPS)
A completed key register should be recorded on the CP documentation and supplied with this B form.
All tests completed |  | Yes/No |  | Sheet 1 of
|  | Signed | Print | Date
Authorised Person (MGPS)
Competent Person (MGPS)

## B32
B32 "Do not use" plugs removed
All testing and commissioning has been successfully completed, and the system is ready for handover to the clinical team.
Location |  | Gas | Number of terminal units | Plugs removed | AP initial
Page 1 of
| Signed |  | Print |  | Date
Authorised Person (MGPS)
Competent Person (MGPS)

## B33
B33 Completion certificate
Testing and commissioning
All tests and inspections as identified on form B0 (record of tests) have been completed and passed.
No further remedial or corrective action is required to be undertaken
All engineering and QC tests have passed and the permit to work form is completed.
Permit to work number
The system is ready for clinical use
| Signed |  | Print |  | Date
Competent Person (MGPS)
Authorised Person (MGPS)
Mechanical Contractor
Quality Controller (MGPS)
Authorising Engineer (MGPS)
These medical gas works have been completed and accepted for clinical use
Print |  | Signed |  | Date
Position
B